## Notes
Update Notes
V 0.02 15-Nov-2013 RTM, changed ISM variable names and added a couple extra unoccupied input variables
V 0.01 14-Nov-2013 RTM Cleaned up old spreadsheet, removed PV, district heating and cooling
V 0.01 14-Nov-2013 RTM Added page that generates the ism file. Now all that needs to be done is to export or copy that sheet to a .ISM file

## ismfile
# ISM generated on 20 -Nov-2013 from primary_school.xlsx
# Building Type = PrimarySchool 2010 located in c:\epw\ord.epw
weatherFilePath = ORD
# Terrain class urban/city = 0.8, suburban/some shielding = 0.9, country/open = 1.0
terrainClass = 0.8
# building height is in m, floor area is in m^2, people density is m2/person
buildingHeight = 4
floorArea = 6871
peopleDensityOccupied = 6.24
peopleDensityUnoccupied = 143
occupancyDayStart = 0
occupancyDayEnd = 4
occupancyHourStart= 8
occupancyHourEnd= 17
# LPD, EPD, GPD all in W/m2, ext light power in W, an heat gain is W/person
lightingPowerDensityOccupied = 7.18
lightingPowerDensityUnoccupied = 0.94
electricAppliancePowerDensityOccupied = 9.9
electricAppliancePowerDensityUnoccupied = 3.77
gasAppliancePowerDensityOccupied = 4.06
gasAppliancePowerDensityUnoccupied = 0
exteriorLightingPower = 1131
heatGainPerPerson = 120
# daylight sensors, occupancy sensors, illum control are set to 1 if there is no control. See iso 15193 Annex F/G for values
daylightSensorSystem= 1
lightingOccupancySensorSystem= 1
constantIlluminationControl= 1
# Temp set points in degrees C
heatingSetpointOccupied = 20.6
heatingSetpointUnoccupied = 16.4
coolingSetpointOccupied = 24.2
coolingSetpointUnoccupied = 26.3
# HVAC waste, heating and cooling loss factors set by HVAC type from EN 15243
hvacWasteFactor= 0
hvacHeatingLossFactor= 0.08
hvacCoolingLossFactor= 0
# COP is W/W, coolingSystemIPLV is the ratio of IPLV/COP
coolingSystemCOP= 3
coolingSystemIPLVToCopRatio= 1.05
#energycarrier is 1 if electric, 2 if gas
heatingFuelType= 2
heatingSystemEfficiency= 0.8
# vent type is 1 if mech, 2 if natural, 3 if mixed, flow rates in m^3/hr
ventilationType = 1
# ventilation flow rates in L/s, default is 10 L/s/person ~ 20 cfm/person
ventilationIntakeRateOccupied= 12246
ventilationIntakeRateUnoccupied= 12246
ventilationExhaustRateOccupied= 12246
ventilationExhaustRateUnoccupied= 12246
# heatRecover = efficiency of heat recovery (0 for none), exhaustAirRecir = fraction of supply air recirculated
heatRecovery= 0
exhaustAirRecirculation= 0
# DHW demand in m3/yr use 10 m3/yr/person as a default for offices
dhwDemand= 268
# dhwDistribution efficiency all taps w/i 3m = 1, taps more than 3m = 0.8, circulation or unknown = 0.6, see NEN 2916 12.6,
dhwSystemEfficiency= 0.8
dhwDistributionEfficiency= 0.8
dhwFuelType= 2
# Surface Heat capacity in J/K/m2
interiorHeatCapacity= 98010
exteriorHeatCapacity= 28921
# BEM type 1= none, 2 = simple, 3=advanced with FDD
bemType= 1
# specific fan power in L/s/W, flow control factor is energy reduction from fan control measures
specificFanPower= 0.51
# fan flow control 1= no control, 0.75 = inlet blade adjuct, 0.65= variable speed see NEN 2916 7.3.3.4
fanFlowcontrolFactor= 1
# infiltration in m3/m2/hr based on surface area
infiltrationRateOccupied= 5.41
infiltrationRateUnoccupied= 5.41
# pump control 0= no pump, 0.5 = auto pump controls for more 50% of pumps, 1.0 = all other cases. See NEN 2914 9.4.3
heatingPumpControl= 1
coolingPumpControl= 1
# Areas in m2, U values in W/m2/K
# SCF = solar control factor (external control), SDF = shading device factor = internal shading
roofArea= 6871
roofUValue= 0.27
roofSolarAbsorption= 0.7
roofThermalEmissivity= 0.9
skylightArea= 0
skylightUValue= 0
skylightSHGC= 0
skylightSCF= 1
skylightSDF= 1
WallAreaS= 603.2
WallUvalueS= 0.363
WallSolarAbsorptionS= 0.7
WallThermalEmissivityS= 0.9
WallAreaSE= 0
WallUvalueSE= 0.363
WallSolarAbsorptionSE= 0.7
WallThermalEmissivitySE= 0.9
WallAreaE= 213.2
WallUvalueE= 0.363
WallSolarAbsorptionE= 0.7
WallThermalEmissivityE= 0.9
WallAreaNE= 0
WallUvalueNE= 0.363
WallSolarAbsorptionNE= 0.7
WallThermalEmissivityNE= 0.9
WallAreaN= 603.2
WallUvalueN= 0.363
WallSolarAbsorptionN= 0.7
WallThermalEmissivityN= 0.9
WallAreaNW= 0
WallUvalueNW= 0.363
WallSolarAbsorptionNW= 0.7
WallThermalEmissivityNW= 0.9
WallAreaW= 213.2
WallUvalueW= 0.363
WallSolarAbsorptionW= 0.7
WallThermalEmissivityW= 0.9
WallAreaSW= 0
WallUvalueSW= 0.27
WallSolarAbsorptionSW= 0.7
WallThermalEmissivitySW= 0.9
WindowAreaS= 324.8
WindowUValueS= 2.653
WindowSHGCS= 0.426
WindowSCFS= 1
WindowSDFS= 1
WindowAreaSE= 0
WindowUValueSE= 2.653
WindowSHGCSE= 0.426
WindowSCFSE= 1
WindowSDFSE= 1
WindowAreaE= 114.8
WindowUValueE= 2.653
WindowSHGCE= 0.426
WindowSCFE= 1
WindowSDFE= 1
WindowAreaNE= 0
WindowUValueNE= 2.653
WindowSHGCNE= 0.426
WindowSCFNE= 1
WindowSDFNE= 1
WindowAreaN= 324.8
WindowUValueN= 2.653
WindowSHGCN= 0.426
WindowSCFN= 1
WindowSDFN= 1
WindowAreaNW= 0
WindowUValueNW= 2.653
WindowSHGCNW= 0.426
WindowSCFNW= 1
WindowSDFNW= 1
WindowAreaW= 115
WindowUValueW= 2.653
WindowSHGCW= 0.426
WindowSCFW= 1
WindowSDFW= 1
WindowAreaSW= 0
WindowUValueSW= 2.653
WindowSHGCSW= 0.426
WindowSCFSW= 1
WindowSDFSW= 1

## Inputs
Hourly & Monthly Energy Calculation Inputs - Non Residential |  |  |  | EUI = 136.3 kWh/m2 = 43.2 kBtu/ft2
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | PrimarySchool
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the primary school from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | Natural gas is used in kitchen so there are gas appliances
Building Height [m] | 4 |  |  | This assumes school is used in summer as well
Total building conditioned floor area [m2] | 6871 |  |  | HVAC is a PTAC with gas heating
People Density: Occ (m2/person) | 6.24 |  |  | Occupany is 1477 people
People Density: Unocc (m2/person) | 143
Building occupancy day - From: | 0
Building occupancy day - To: | 4
Equivalent full-load occupancy hours - From: | 8
Equivalent full-load occupancy hours - To: | 17
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 20.6 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 16.4 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.2 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 26.3 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 9.9 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 3.77 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 4.06 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 7.18 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 0.94 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 1131 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 3 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1.05 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 12246 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 12246 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 12246 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 12246 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 1 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.51 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 268 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 28921
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 5.41
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 5.41
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 603.2 | 0 | 213.2 | 0 | 603.2 | 0 | 213.2 | 0 | 6871
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 324.8 | 0 | 114.8 | 0 | 324.8 | 0 | 115 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 5.41 S to 5.41 Roof
Shading Device Factor (SDF) | bar: 5.41 S to 5.41 Roof
Area Summary | 5.41 S: m2; 5.41 SE: ft2
Total roof area [m2] | 5.41 S: 6871; 5.41 SE: 73794.54
Total opaque wall area [m2] | 5.41 S: 1632.8; 5.41 SE: 17536.272
Total window [m2] | 5.41 S: 879.4; 5.41 SE: 9444.756
Total Envelope Area [m2] | 5.41 S: 9383.2; 5.41 SE: 100775.568
Window to Wall Ratio | 5.41 S: 0.35005
IPLV Calculator | bar: 5.41 S to 5.41 SE
Relative COP100: for Relative Load 100% | 5.41 S: 1; 5.41 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 5.41 S: 0.9; 5.41 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 5.41 S: 0.82; 5.41 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 5.41 S: 0.5; 5.41 SE: Refer to the right figure
Weighting of 100% Load | 5.41 S: 0.01; 5.41 SE: From ARI 550/590
Weighting of 75% Load | 5.41 S: 0.42; 5.41 SE: From ARI 550/591
Weighting of 50% Load | 5.41 S: 0.45; 5.41 SE: From ARI 550/592
Weighting of 25% Load | 5.41 S: 0.12; 5.41 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 5.41 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## PrimarySchool
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | PrimarySchool
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the primary school from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | Natural gas is used in kitchen so there are gas appliances
Building Height [m] | 4 |  |  | This assumes school is used in summer as well
Total building conditioned floor area [m2] | 6871 |  |  | HVAC is a PTAC with gas heating
People Density: Occ (m2/person) | 6.24 |  |  | Occupany is 1477 people
People Density: Unocc (m2/person) | 143
Building occupancy day - From: | 0
Building occupancy day - To: | 4
Equivalent full-load occupancy hours - From: | 8
Equivalent full-load occupancy hours - To: | 17
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 20.6 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 16.4 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.2 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 26.3 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 9.9 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 3.77 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 4.06 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 7.18 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 0.94 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 1131 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 3 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1.05 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 12246 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 12246 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 12246 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 12246 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 1 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.51 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 268 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 28921
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 5.41
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 5.41
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 603.2 | 0 | 213.2 | 0 | 603.2 | 0 | 213.2 | 0 | 6871
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 324.8 | 0 | 114.8 | 0 | 324.8 | 0 | 115 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 5.41 S to 5.41 Roof
Shading Device Factor (SDF) | bar: 5.41 S to 5.41 Roof
Area Summary | 5.41 S: m2; 5.41 SE: ft2
Total roof area [m2] | 5.41 S: 6871; 5.41 SE: 73794.54
Total opaque wall area [m2] | 5.41 S: 1632.8; 5.41 SE: 17536.272
Total window [m2] | 5.41 S: 879.4; 5.41 SE: 9444.756
Total Envelope Area [m2] | 5.41 S: 9383.2; 5.41 SE: 100775.568
Window to Wall Ratio | 5.41 S: 0.35005
IPLV Calculator | bar: 5.41 S to 5.41 SE
Relative COP100: for Relative Load 100% | 5.41 S: 1; 5.41 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 5.41 S: 0.9; 5.41 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 5.41 S: 0.82; 5.41 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 5.41 S: 0.5; 5.41 SE: Refer to the right figure
Weighting of 100% Load | 5.41 S: 0.01; 5.41 SE: From ARI 550/590
Weighting of 75% Load | 5.41 S: 0.42; 5.41 SE: From ARI 550/591
Weighting of 50% Load | 5.41 S: 0.45; 5.41 SE: From ARI 550/592
Weighting of 25% Load | 5.41 S: 0.12; 5.41 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 5.41 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## AptMidrise
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | AptMidrise
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the Midrise Apartment from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | HVAC values were tweaked to reflect individual AC units with central gas heat and individual controls
Building Height [m] | 12.19 |  |  | Setback temps reflect setback only in offices and hallways
Total building conditioned floor area [m2] | 3134 |  |  | Full load Occupancy is 7 days a week, 17 hours a day (less weekdays, more weekends)
People Density: Occ (m2/person) | 66.87 |  |  | Occupancy is 79 people total
People Density: Unocc (m2/person) | 43.26
Building occupancy day - From: | 0
Building occupancy day - To: | 6
Equivalent full-load occupancy hours - From: | 0
Equivalent full-load occupancy hours - To: | 17
Heat Gain per Person [W/person] | 95
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21.5 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 21.4 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.5 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 24.6 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 3.61 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 4.87 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 0.97 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 1.36 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 1270 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 5 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 858 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 858 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 858 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 858 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 0 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.89 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 1874 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 1 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 46324
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 7.6
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 7.6
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 481.6 | 0 | 172.56 | 0 | 481.6 | 0 | 172.56 | 0 | 783.66
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 83.2 | 0 | 33.66 | 0 | 83.2 | 0 | 33.66 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 7.6 S to 7.6 Roof
Shading Device Factor (SDF) | bar: 7.6 S to 7.6 Roof
Area Summary | 7.6 S: m2; 7.6 SE: ft2
Total roof area [m2] | 7.6 S: 783.66; 7.6 SE: 8416.5084
Total opaque wall area [m2] | 7.6 S: 1538.04; 7.6 SE: 16518.5496
Total window [m2] | 7.6 S: 233.72; 7.6 SE: 2510.1528
Total Envelope Area [m2] | 7.6 S: 2555.42; 7.6 SE: 27445.2108
Window to Wall Ratio | 7.6 S: 0.13191
IPLV Calculator | bar: 7.6 S to 7.6 SE
Relative COP100: for Relative Load 100% | 7.6 S: 1; 7.6 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 7.6 S: 0.9; 7.6 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 7.6 S: 0.82; 7.6 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 7.6 S: 0.5; 7.6 SE: Refer to the right figure
Weighting of 100% Load | 7.6 S: 0.01; 7.6 SE: From ARI 550/590
Weighting of 75% Load | 7.6 S: 0.42; 7.6 SE: From ARI 550/591
Weighting of 50% Load | 7.6 S: 0.45; 7.6 SE: From ARI 550/592
Weighting of 25% Load | 7.6 S: 0.12; 7.6 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 7.6 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## AptHighrise
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | AptHighrise
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the Highrise Apartment from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | HVAC values were tweaked to reflect individual AC units with central gas heat and individual controls
Building Height [m] | 30.48 |  |  | Setback temps are implemented (not done in PNNL reference building)
Total building conditioned floor area [m2] | 7836.6 |  |  | Full load Occupancy is 7 days a week, 17 hours a day (less weekdays, more weekends)
People Density: Occ (m2/person) | 65.88 |  |  | Occupany is 199 people
People Density: Unocc (m2/person) | 42.44 |  |  | Ventilation rate set at 10L/s/person because value extracted automatically comes from incorrect Table.csv
Building occupancy day - From: | 0
Building occupancy day - To: | 6
Equivalent full-load occupancy hours - From: | 0
Equivalent full-load occupancy hours - To: | 17
Heat Gain per Person [W/person] | 95
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21.7 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 17.7 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.4 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 29.4 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 3.61 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 4.93 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 0.87 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 1.28 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 1270 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 5 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 2000 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 2000 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 2000 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 2000 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 0 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.89 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 4778 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 1 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 46324
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 7
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 7
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 1204 | 0 | 431.4 | 0 | 1204 | 0 | 431.4 | 0 | 783.66
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 208 | 0 | 84.15 | 0 | 208 | 0 | 84.15 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 7 S to 7 Roof
Shading Device Factor (SDF) | bar: 7 S to 7 Roof
Area Summary | 7 S: m2; 7 SE: ft2
Total roof area [m2] | 7 S: 783.66; 7 SE: 8416.5084
Total opaque wall area [m2] | 7 S: 3270.8; 7 SE: 35128.392
Total window [m2] | 7 S: 584.3; 7 SE: 6275.382
Total Envelope Area [m2] | 7 S: 4638.76; 7 SE: 49820.2824
Window to Wall Ratio | 7 S: 0.15157
IPLV Calculator | bar: 7 S to 7 SE
Relative COP100: for Relative Load 100% | 7 S: 1; 7 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 7 S: 0.9; 7 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 7 S: 0.82; 7 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 7 S: 0.5; 7 SE: Refer to the right figure
Weighting of 100% Load | 7 S: 0.01; 7 SE: From ARI 550/590
Weighting of 75% Load | 7 S: 0.42; 7 SE: From ARI 550/591
Weighting of 50% Load | 7 S: 0.45; 7 SE: From ARI 550/592
Weighting of 25% Load | 7 S: 0.12; 7 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 7 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## OfficeSmall
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | OfficeSmall
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from theSmall Office from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | Height includes peaked roof - zone height is only 3.1 m
Building Height [m] | 3.1 |  |  | Occupancy is 31 people
Total building conditioned floor area [m2] | 511 |  |  | HVAC is air source heat pumps for heating and cooling with constant volume AHU so use type 18
People Density: Occ (m2/person) | 21.2 |  |  | Use roof U=0.27 because it is not extracted properly since it is an attic space
People Density: Unocc (m2/person) | 732
Building occupancy day - From: | 0
Building occupancy day - To: | 4
Equivalent full-load occupancy hours - From: | 7
Equivalent full-load occupancy hours - To: | 18
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21.1 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 15.7 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.3 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 29.3 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 5.52 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 1.74 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 7.2 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 1.93 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 304 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 18 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 3.2 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 1 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 2.13 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 3 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 159 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 159 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 159 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 159 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 0 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 0 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.89 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 31 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 38253
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 7.1
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 7.1
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 67.71 | 0 | 45.14 | 0 | 67.71 | 0 | 45.14 | 0 | 599
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 20.65 | 0 | 11.16 | 0 | 16.74 | 0 | 11.16 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 7.1 S to 7.1 Roof
Shading Device Factor (SDF) | bar: 7.1 S to 7.1 Roof
Area Summary | 7.1 S: m2; 7.1 SE: ft2
Total roof area [m2] | 7.1 S: 599; 7.1 SE: 6433.26
Total opaque wall area [m2] | 7.1 S: 225.7; 7.1 SE: 2424.018
Total window [m2] | 7.1 S: 59.71; 7.1 SE: 641.2854
Total Envelope Area [m2] | 7.1 S: 884.41; 7.1 SE: 9498.5634
Window to Wall Ratio | 7.1 S: 0.20921
IPLV Calculator | bar: 7.1 S to 7.1 SE
Relative COP100: for Relative Load 100% | 7.1 S: 1; 7.1 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 7.1 S: 0.9; 7.1 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 7.1 S: 0.82; 7.1 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 7.1 S: 0.5; 7.1 SE: Refer to the right figure
Weighting of 100% Load | 7.1 S: 0.01; 7.1 SE: From ARI 550/590
Weighting of 75% Load | 7.1 S: 0.42; 7.1 SE: From ARI 550/591
Weighting of 50% Load | 7.1 S: 0.45; 7.1 SE: From ARI 550/592
Weighting of 25% Load | 7.1 S: 0.12; 7.1 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 7.1 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## OfficeLarge
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | LargeOffice
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the Office Large from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | DHW use set at1 m3/person/year
Building Height [m] | 39.94 |  |  | Population is 2493 occupants
Total building conditioned floor area [m2] | 46320.43
People Density: Occ (m2/person) | 24.03
People Density: Unocc (m2/person) | 344
Building occupancy day - From: | 0
Building occupancy day - To: | 4
Equivalent full-load occupancy hours - From: | 8
Equivalent full-load occupancy hours - To: | 18
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 17.4 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 25.9 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 6.07 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 2.61 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 7.28 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 0.96 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 17485 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 5.86 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1.13 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.81 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 3 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 28040 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 28040 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 28040 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 28040 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 1 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.89 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 2493 |  |  | Scroll
DHW System Efficiency | 1 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 1 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 239755
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 1.8
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 1.8
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 2086 | 0 | 1390.67 | 0 | 2086 | 0 | 1390.67 | 0 | 3563.11
U-value | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 1390.84 | 0 | 927.33 | 0 | 1390.84 | 0 | 927.33 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 1.8 S to 1.8 Roof
Shading Device Factor (SDF) | bar: 1.8 S to 1.8 Roof
Area Summary | 1.8 S: m2; 1.8 SE: ft2
Total roof area [m2] | 1.8 S: 3563.11; 1.8 SE: 38267.8014
Total opaque wall area [m2] | 1.8 S: 6953.34; 1.8 SE: 74678.8716
Total window [m2] | 1.8 S: 4636.34; 1.8 SE: 49794.2916
Total Envelope Area [m2] | 1.8 S: 15152.79; 1.8 SE: 162740.9646
Window to Wall Ratio | 1.8 S: 0.40004
IPLV Calculator | bar: 1.8 S to 1.8 SE
Relative COP100: for Relative Load 100% | 1.8 S: 1; 1.8 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 1.8 S: 0.9; 1.8 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 1.8 S: 0.82; 1.8 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 1.8 S: 0.5; 1.8 SE: Refer to the right figure
Weighting of 100% Load | 1.8 S: 0.01; 1.8 SE: From ARI 550/590
Weighting of 75% Load | 1.8 S: 0.42; 1.8 SE: From ARI 550/591
Weighting of 50% Load | 1.8 S: 0.45; 1.8 SE: From ARI 550/592
Weighting of 25% Load | 1.8 S: 0.12; 1.8 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 1.8 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## Outputs
DELIVERED ENERGY PERFORMANCE | [11 empty] | OUTPUT SUMMARY
Total Delivered Energy | [11 empty] | 1.Energy Use Intensity |  | SI |  | IP
Month | Eheat [kWh/m2] | ECool [kWh/m2] | Eint_light [kWh/m2] | Eext_light [kWh/m2] | Efan [kWh/m2] | Epump [kWh/m2] | Eplug [kWh/m2] | EDHW [kWh/m2] | Egen [kWh/m2] | Etotal [kWh/m2] | Etotal [kWh] | EUI: Heating Need | 11.6946 | kWh/m2/yr | 3.7072 | kBTU/ft2/yr
Jan | 5.261 | 0.25588 | 2.1561 | 0.05613 | 0.21977 | 0.22735 | 4.8356 | 0.23973 | 0 | 13.2515 | 91050.9364 | EUI: Cooling Need | 80.245 | kWh/m2/yr | 25.4375 | kBTU/ft2/yr
Feb | 3.3879 | 0.34225 | 1.9474 | 0.050698 | 0.17624 | 0.17343 | 4.3676 | 0.21653 | 0 | 10.6621 | 73259.1063 | EUI: Total Thermal Need | 91.9396 | kWh/m2/yr | 29.1447 | kBTU/ft2/yr
Mar | 1.214 | 0.84179 | 2.1561 | 0.05613 | 0.20069 | 0.17165 | 4.8356 | 0.23973 | 0 | 9.7157 | 66756.5921 | EUI: Delivered Electricity | 108.2049 | kWh/m2/yr | 34.3008 | kBTU/ft2/yr
Apr | 0.18466 | 1.7338 | 2.0865 | 0.05432 | 0.32987 | 0.27062 | 4.6796 | 0.232 | 0 | 9.5714 | 65764.8147 | EUI: Delivered Natural Gas | 28.0926 | kWh/m2/yr | 8.9053 | kBTU/ft2/yr
May | 0.0032664 | 3.1257 | 2.1561 | 0.05613 | 0.55768 | 0.47608 | 4.8356 | 0.23973 | 0 | 11.4502 | 78674.5964 | EUI: Total Delivered | 136.2975 | kWh/m2/yr | 43.2061 | kBTU/ft2/yr
Jun | 0 | 4.0423 | 2.0865 | 0.05432 | 0.67017 | 0.61554 | 4.6796 | 0.232 | 0 | 12.3805 | 85066.1347 | EUI: Total Primary | 394.7866 | kWh/m2/yr | 125.1467 | kBTU/ft2/yr
Jul | 0 | 4.7988 | 2.1561 | 0.05613 | 0.77895 | 0.73073 | 4.8356 | 0.23973 | 0 | 13.596 | 93418.1449
Aug | 0 | 4.1852 | 2.1561 | 0.05613 | 0.69351 | 0.63729 | 4.8356 | 0.23973 | 0 | 12.8035 | 87972.7971 | 2. Energy Consumption
Sep | 5.8554e-05 | 3.2974 | 2.0865 | 0.05432 | 0.57108 | 0.50211 | 4.6796 | 0.232 | 0 | 11.4231 | 78488.3562 | Energy Consumption: Delivered Electricity | 743.476 | MWh/yr | 743.476 | MWh/yr
Oct | 0.13305 | 1.8067 | 2.1561 | 0.05613 | 0.34115 | 0.27988 | 4.8356 | 0.23973 | 0 | 9.8484 | 67668.0173 | Energy Consumption: Delivered Natural Gas | 193.024 | MWh/yr | 6.5863 | Therm/yr
Nov | 1.1226 | 0.68524 | 2.0865 | 0.05432 | 0.1753 | 0.14454 | 4.6796 | 0.232 | 0 | 9.1802 | 63076.8209 | Energy Consumption: Total Delivered | 936.4999 | MWh/yr | 3.1955 | MBTU/yr
Dec | 4.4369 | 0.28825 | 2.1561 | 0.05613 | 0.19954 | 0.20277 | 4.8356 | 0.23973 | 0 | 12.415 | 85303.6285
Total | 15.7434 | 25.4033 | 25.386 | 0.66089 | 4.9139 | 4.432 | 56.9353 | 2.8226 | 0 | 136.2975 | 936499.9454 | 3. Primary Energy
[12 empty] | Consumption: Source Electricity | 2501.7967 | MWh/yr | 8.5365 | MBTU/yr
[12 empty] | Consumption: Source Natural Gas | 210.7822 | MWh/yr | 0.71922 | MBTU/yr
Electricity | [11 empty] | Energy Consumption: Total Primary | 2712.5789 | MWh/yr | 9.2557 | MBTU/yr
Month | Eheat [kWh/m2] | ECool [kWh/m2] | Eint_light [kWh/m2] | Eext_light [kWh/m2] | Efan [kWh/m2] | Epump [kWh/m2] | Eplug [kWh/m2] | EDHW [kWh/m2] | Egen [kWh/m2] | Etotal [kWh/m2] | Etotal [kWh]
Jan | 0 | 0.25588 | 2.1561 | 0.05613 | 0.21977 | 0.22735 | 4.0265 | 0 | 0 | 6.9417 | 47696.3828 | 4. Emissions
Feb | 0 | 0.34225 | 1.9474 | 0.050698 | 0.17624 | 0.17343 | 3.6368 | 0 | 0 | 6.3269 | 43471.9454 | Emissions: CO2 | 488.6871 | ton/yr | 488.6871 | ton/yr
Mar | 0 | 0.84179 | 2.1561 | 0.05613 | 0.20069 | 0.17165 | 4.0265 | 0 | 0 | 7.4528 | 51208.4712 | Emissions: NOx | 0.8704 | ton/yr | 0.8704 | ton/yr
Apr | 0 | 1.7338 | 2.0865 | 0.05432 | 0.32987 | 0.27062 | 3.8966 | 0 | 0 | 8.3717 | 57522.0009 | Emissions: SOx | 1.9662 | ton/yr | 1.9662 | ton/yr
May | 0 | 3.1257 | 2.1561 | 0.05613 | 0.55768 | 0.47608 | 4.0265 | 0 | 0 | 10.3981 | 71445.6518
Jun | 0 | 4.0423 | 2.0865 | 0.05432 | 0.67017 | 0.61554 | 3.8966 | 0 | 0 | 11.3655 | 78092.1016 | 5. Reference Values
Jul | 0 | 4.7988 | 2.1561 | 0.05613 | 0.77895 | 0.73073 | 4.0265 | 0 | 0 | 12.5472 | 86211.644 | E_ref_nd | 118 | kWh/m2/yr | 37.4058 | kBTU/ft2/yr
Aug | 0 | 4.1852 | 2.1561 | 0.05613 | 0.69351 | 0.63729 | 4.0265 | 0 | 0 | 11.7547 | 80766.2962 | E_ref_del | 200 | kWh/m2/yr | 63.3997 | kBTU/ft2/yr
Sep | 0 | 3.2974 | 2.0865 | 0.05432 | 0.57108 | 0.50211 | 3.8966 | 0 | 0 | 10.4081 | 71513.9207 | E_ref_pri | 468.8701 | kWh/m2/yr | 148.6311 | kBTU/ft2/yr
Oct | 0 | 1.8067 | 2.1561 | 0.05613 | 0.34115 | 0.27988 | 4.0265 | 0 | 0 | 8.6665 | 59547.3389
Nov | 0 | 0.68524 | 2.0865 | 0.05432 | 0.1753 | 0.14454 | 3.8966 | 0 | 0 | 7.0425 | 48389.2393 | 6. EPC
Dec | 0 | 0.28825 | 2.1561 | 0.05613 | 0.19954 | 0.20277 | 4.0265 | 0 | 0 | 6.9293 | 47610.9963 | EPC: Thermal Need | 0.77915 |  | 0.77915
Total | 0 | 25.4033 | 25.386 | 0.66089 | 4.9139 | 4.432 | 47.4088 | 0 | 0 | 108.2049 | 743475.9889 | EPC: Delivered | 0.68149 |  | 0.68149
[12 empty] | EPC: Primary | 0.842 |  | 0.842
Natural Gas
Month | Eheat [kWh/m2] | ECool [kWh/m2] | Eint_light [kWh/m2] | Eext_light [kWh/m2] | Efan [kWh/m2] | Epump [kWh/m2] | Eplug [kWh/m2] | EDHW [kWh/m2] | Egen [kWh/m2] | Etotal [kWh/m2] | Etotal [kWh]
Jan | 5.261 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 6.3098 | 43354.5536
Feb | 3.3879 | 0 |  |  |  |  | 0.7308 | 0.21653 |  | 4.3352 | 29787.1609
Mar | 1.214 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 2.2629 | 15548.1209
Apr | 0.18466 | 0 |  |  |  |  | 0.783 | 0.232 |  | 1.1997 | 8242.8138
May | 0.0032664 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 1.0521 | 7228.9446
Jun | 0 | 0 |  |  |  |  | 0.783 | 0.232 |  | 1.015 | 6974.0331
Jul | 0 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 1.0488 | 7206.5009
Aug | 0 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 1.0488 | 7206.5009
Sep | 5.8554e-05 | 0 |  |  |  |  | 0.783 | 0.232 |  | 1.0151 | 6974.4355
Oct | 0.13305 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 1.1819 | 8120.6784
Nov | 1.1226 | 0 |  |  |  |  | 0.783 | 0.232 |  | 2.1376 | 14687.5816
Dec | 4.4369 | 0 |  |  |  |  | 0.8091 | 0.23973 |  | 5.4858 | 37692.6322
Total | 15.7434 | 0 | 0 |  | 0 | 0 | 9.5265 | 2.8226 | 0 | 28.0926 | 193023.9565

## Calcs (hidden)
DATA for Calculation
| Gross Floor Area (m2) | 6871
Schedule and Occupancy | [11 empty] | Constants | [13 empty] | Time in Msec | [16 empty] | Monthly Ave Temps for Each Hour | [23 empty] | Monthly avg horizontal radiation for each hour | [32 empty] | Solar radiation fraction
[14 empty] | Duration of calculation (Ms) by EN ISO 13790 Annex A | Duration of calculation (hrs) | Days |  | Primary Energy Factor: Electricity |  | 3.365 | [5 empty] | Occupied | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night |  |  | Monthly Average Temp ( C ) | Monthly Average Wind Speed ( m/s) | Global S(W/m2) | Global SE (W/m2) | Global E(W/m2) | Global NE(W/m2) | Global N(W/m2) | Global NW (W/m2) | Global West (W/m2) | Global SW (W/m2) | Global horizontal radiation (W/m2) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Te_unocc_daytime | Te_unocc_night | R_daytime (W/m2) | R_unocc_weekday_night (W/m2) | R_occupied_daytime (MJ/m2) | R_unocc_weekday_night (MJ/m2) | R_unocc_weekend_daytime (MJ/m2) | R_unocc_weekend_night (MJ/m2) | Total (MJ/m2) | Occupied | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night
| Occupancy | Operation hours |  |  | Operation days | [7 empty] | Jan | 2.6784 | 744 | 31 |  | Primary Energy Factor: Natural Gas |  | 1.092 |  |  |  |  | Jan | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | Jan | -4.645 | 4.8803 | 125.2987 | 87.4701 | 43.0253 | 23.676 | 23.013 | 26.2917 | 58.8181 | 107.3479 | 73.5976 | -6.2839 | -6.1806 | -6.0871 | -6.2742 | -6.5226 | -6.8065 | -6.7806 | -6.5581 | -5.5516 | -4.3613 | -3.5452 | -2.7903 | -2.029 | -1.6839 | -1.5968 | -1.8613 | -2.9129 | -3.8258 | -4.5452 | -4.5097 | -4.7097 | -4.9774 | -5.2387 | -5.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3226 | 92.871 | 191.2258 | 260.129 | 302.7419 | 305.9032 | 276.7742 | 192.5161 | 98.8065 | 22.6774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.3308 | -5.4361 | 193.4767 | 1.5118 | 138.8057 | 1.4462 | 55.5223 | 1.0846 | 196.8588 | 0.7051 | 0.0073462 | 0.28204 | 0.0055097
|  | Start | 8 |  | Start | 0 | [6 empty] | Feb | 2.4192 | 672 | 28 | [8 empty] | Feb | 0.648 | 0.864 | 0.2592 | 0.648 |  | Feb | -2.5292 | 5.0704 | 143.2794 | 105.532 | 60.4409 | 34.6711 | 32.0986 | 40.1465 | 79.4993 | 127.1273 | 103.8899 | -3.6571 | -3.9286 | -4.1464 | -4.4643 | -4.9071 | -5.1214 | -5.2643 | -4.625 | -3.2929 | -2.0964 | -1.0214 | -0.24286 | 0.25714 | 0.39643 | 0.49643 | 0.26071 | -0.46429 | -1.425 | -2.3464 | -2.5821 | -2.85 | -2.925 | -3.15 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0714 | 48.25 | 149.5 | 271.3929 | 364.5 | 390.3929 | 395.1786 | 342.2857 | 273.9286 | 179.6429 | 67.6071 | 7.6071 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0964 | -3.3888 | 268.3413 | 5.219 | 173.8851 | 4.5093 | 69.5541 | 3.3819 | 251.3304 | 0.69186 | 0.017942 | 0.27674 | 0.013456
|  | End | 17 |  | End | 5 | [6 empty] | Mar | 2.6784 | 744 | 31 |  | Emission Factors for Delivered Electricity | [6 empty] | Mar | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | Mar | 3.825 | 5.4858 | 146.2056 | 121.7475 | 84.7544 | 51.7841 | 42.8237 | 58.9952 | 99.9558 | 135.9106 | 143.3401 | 2.0226 | 1.8161 | 1.7677 | 1.2484 | 1.1323 | 0.91935 | 1.4226 | 2.7548 | 3.9677 | 5.0548 | 5.9387 | 6.8194 | 7.1871 | 7.3258 | 7.1935 | 6.7677 | 6.1355 | 5.0387 | 3.9419 | 3.3 | 2.9419 | 2.6097 | 2.3742 | 2.1194 | 0 | 0 | 0 | 0 | 0 | 0.58065 | 31.7742 | 132 | 241.4194 | 368.4839 | 455.5161 | 479.7097 | 503.9032 | 451.0968 | 361.0323 | 252.9032 | 128.0645 | 33.129 | 0.54839 | 0 | 0 | 0 | 0 | 0 | 5.89 | 2.586 | 360.6738 | 12.9398 | 258.7577 | 12.3778 | 103.5031 | 9.2834 | 383.922 | 0.67399 | 0.03224 | 0.26959 | 0.02418
|  | Operation hours | 9 |  | Operation days | 5 | [6 empty] | Apr | 2.592 | 720 | 30 |  |  |  | per delivered electricity |  |  |  |  | Apr | 0.69429 | 0.92571 | 0.27771 | 0.69429 |  | Apr | 9.9386 | 4.8403 | 129.5457 | 123.9194 | 104.9122 | 71.359 | 54.1235 | 84.556 | 124.645 | 138.2998 | 183.0889 | 7.7933 | 7.6133 | 7.5633 | 7.1933 | 6.9567 | 7.0367 | 8.0933 | 9.2567 | 10.1867 | 10.9467 | 11.7933 | 12.2767 | 12.7633 | 13.12 | 13.0133 | 12.84 | 12.41 | 11.5033 | 10.5767 | 9.88 | 9.4867 | 9.18 | 8.9167 | 8.1267 | 0 | 0 | 0 | 0 | 0 | 7.1333 | 148.4 | 241.5333 | 371.5333 | 463.8 | 516.1 | 548.5333 | 519.5 | 528.9333 | 438.9333 | 327.9333 | 193.5667 | 85.5333 | 2.7 | 0 | 0 | 0 | 0 | 0 | 11.7996 | 8.822 | 439.6444 | 29.1556 | 305.2389 | 26.9897 | 122.0955 | 20.2423 | 474.5664 | 0.6432 | 0.056872 | 0.25728 | 0.042654
[13 empty] | May | 2.6784 | 744 | 31 |  | CO2 |  | 0.604 | kg/kWh electricity |  |  |  | May | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | May | 15.2972 | 3.7435 | 132.1856 | 143.7596 | 137.9482 | 102.3898 | 76.5605 | 119.7198 | 158.8442 | 155.6002 | 248.9946 | 10.7097 | 10.3161 | 10.1677 | 10.0516 | 9.8935 | 11.2258 | 13.5677 | 15.4742 | 17.2935 | 18.6968 | 19.8194 | 20.5806 | 21.0548 | 20.9452 | 20.5742 | 19.9871 | 19.5323 | 18.0968 | 16.0742 | 14.4871 | 13.3323 | 12.4548 | 11.7613 | 11.0355 | 0 | 0 | 0 | 0 | 8.7419 | 68.5484 | 202.2258 | 355.3226 | 507.2581 | 631.9032 | 680.7419 | 710.5806 | 723.9032 | 670.8065 | 538.2903 | 418.129 | 287.6452 | 135.7742 | 35.4194 | 0.58065 | 0 | 0 | 0 | 0 | 19.3806 | 12.8471 | 581.8817 | 49.2624 | 417.4586 | 47.123 | 166.9834 | 35.3422 | 666.9072 | 0.62596 | 0.070659 | 0.25038 | 0.052994
|  | Occupancy (m2/person) | 6.24 | [9 empty] | Jun | 2.592 | 720 | 30 |  | NOx |  | 0.00112 | kg/kWh electricity |  |  |  | Jun | 0.69429 | 0.92571 | 0.27771 | 0.69429 |  | Jun | 21.11 | 4.8865 | 121.0796 | 143.0968 | 148.0842 | 116.2031 | 87.9684 | 132.1614 | 164.7566 | 150.4755 | 262.2292 | 17.5967 | 17.2533 | 17.2067 | 16.8633 | 16.72 | 17.5933 | 19.5733 | 21.2833 | 22.5033 | 23.59 | 24.3833 | 24.83 | 25.2267 | 25.4667 | 25.39 | 25.1333 | 24.7567 | 23.9567 | 22.3333 | 20.68 | 19.41 | 18.79 | 18.1333 | 17.9667 | 0 | 0 | 0 | 0 | 16.2667 | 95.1 | 232.8333 | 384.4667 | 533.2 | 625.5 | 709.1 | 702.6333 | 698.3333 | 660.9 | 586.8667 | 475.2 | 319.9 | 185.6 | 61.7333 | 5.8667 | 0 | 0 | 0 | 0 | 24.2007 | 19.2556 | 597.3556 | 61.1533 | 414.7354 | 56.6105 | 165.8942 | 42.4579 | 679.698 | 0.61018 | 0.083288 | 0.24407 | 0.062466
|  | Total occupants | 1101.1218 | [9 empty] | July | 2.6784 | 744 | 31 |  | SOx |  | 0.00216 | kg/kWh electricity |  |  |  | Jul | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | July | 24.1296 | 4.2386 | 130.1293 | 142.6802 | 140.7194 | 109.4948 | 85.0596 | 129.5252 | 166.1474 | 158.3957 | 257.3656 | 20.7129 | 20.3419 | 19.871 | 19.7323 | 19.5323 | 20.7065 | 22.4 | 23.7323 | 24.9613 | 26.0774 | 27.0387 | 27.8323 | 28.4419 | 28.5774 | 28.4968 | 27.9806 | 27.3194 | 26.5161 | 25.4 | 24.0484 | 23.2452 | 22.6484 | 22.0419 | 21.4548 | 0 | 0 | 0 | 0 | 8.3871 | 67.5484 | 194.3226 | 338 | 477.0968 | 600.6129 | 664.3548 | 732.2903 | 761.3226 | 681.7097 | 611.1935 | 464.1613 | 333.0323 | 181.129 | 56.8065 | 4.8065 | 0 | 0 | 0 | 0 | 27.0154 | 22.3981 | 592.3047 | 56.4022 | 424.9363 | 53.9527 | 169.9745 | 40.4645 | 689.328 | 0.61645 | 0.078269 | 0.24658 | 0.058701
[13 empty] | Aug | 2.6784 | 744 | 31 | [8 empty] | Aug | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | Aug | 21.7804 | 3.8431 | 136.0947 | 138.7103 | 123.7441 | 88.1775 | 66.2563 | 103.4434 | 143.3642 | 150.8323 | 215.0591 | 18.5935 | 18.3194 | 18.1613 | 17.671 | 17.6645 | 18.029 | 20.0871 | 21.7097 | 23.2581 | 24.6032 | 25.2032 | 25.4323 | 25.9 | 25.7194 | 25.429 | 25.1742 | 24.5387 | 23.771 | 22.3645 | 21.4645 | 20.6 | 20.2742 | 19.5806 | 19.1806 | 0 | 0 | 0 | 0 | 0.32258 | 31.9355 | 138.4516 | 277.8065 | 413.3226 | 548.9677 | 611.0968 | 647.6129 | 624.2581 | 575.9032 | 489.1935 | 407.7097 | 253.0968 | 116.8065 | 24.7742 | 0.16129 | 0 | 0 | 0 | 0 | 24.7143 | 20.02 | 510.6523 | 37.7032 | 366.3566 | 36.0658 | 146.5426 | 27.0494 | 576.0144 | 0.63602 | 0.062613 | 0.25441 | 0.04696
[13 empty] | Sep | 2.592 | 720 | 30 |  | Emission Factors for Delivered Natural Gas | [6 empty] | Sep | 0.69429 | 0.92571 | 0.27771 | 0.69429 |  | Sep | 18.1421 | 3.4178 | 153.3054 | 136.1685 | 103.0097 | 62.644 | 47.8345 | 72.4894 | 118.8972 | 148.4966 | 174.6931 | 14.91 | 14.4867 | 14.14 | 13.88 | 13.7167 | 13.6067 | 15.5367 | 17.65 | 19.3933 | 20.46 | 21.4033 | 22.2433 | 22.8367 | 23.15 | 22.8867 | 22.4867 | 21.5567 | 19.96 | 18.6 | 17.8 | 16.8667 | 16.4967 | 15.8767 | 15.4667 | 0 | 0 | 0 | 0 | 0 | 10.9333 | 86.6333 | 219.0667 | 367.3667 | 479.5333 | 533.8333 | 555.5333 | 558.0333 | 500.5 | 398.0667 | 289.9 | 150.1 | 40.9667 | 2.1667 | 0 | 0 | 0 | 0 | 0 | 21.39 | 16.1933 | 433.537 | 19.3867 | 300.9986 | 17.9465 | 120.3994 | 13.4599 | 452.8044 | 0.66474 | 0.039634 | 0.2659 | 0.029726
|  |  |  | Occupied weekday | Unocc Weekday | Unocc Weekend Daytime | Unocc Weekend Night | Unocc Weekend Total |  |  |  |  | Oct | 2.6784 | 744 | 31 |  |  | precombustion | onsite combustion |  |  |  |  | Oct | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | Oct | 10.9832 | 4.7862 | 153.0695 | 119.8451 | 74.1735 | 39.6366 | 34.5519 | 45.2912 | 87.7809 | 133.4038 | 122.5497 | 8.4968 | 8.229 | 8 | 7.8129 | 7.7968 | 7.5452 | 8.0613 | 9.8774 | 11.7548 | 13.1774 | 14.3258 | 14.9452 | 15.2484 | 15.429 | 15.3452 | 14.6387 | 13.2613 | 11.7645 | 11.0194 | 10.429 | 9.8419 | 9.3387 | 8.7419 | 8.5161 | 0 | 0 | 0 | 0 | 0 | 0.32258 | 33.3871 | 136.0645 | 265.0323 | 374.871 | 424.3548 | 427.9032 | 425.5161 | 378.1935 | 265.871 | 156.9677 | 48.9677 | 3.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8602 | 9.257 | 317.1971 | 5.7613 | 227.5663 | 5.5111 | 91.0265 | 4.1333 | 328.2372 | 0.6933 | 0.01679 | 0.27732 | 0.012592
| Bldg schedule and hours | Days | 7 | 5 | 4 | [7 empty] | Nov | 2.592 | 720 | 30 |  | CO2 | 0.017794 | 0.1875 | kg/kWh NG |  |  |  | Nov | 0.69429 | 0.92571 | 0.27771 | 0.69429 |  | Nov | 4.7393 | 5.2951 | 114.9026 | 84.5355 | 45.2516 | 26.5701 | 25.6212 | 28.7375 | 55.7373 | 97.38 | 75.7764 | 3.7133 | 3.4533 | 3.3567 | 3.3567 | 3.06 | 2.85 | 2.7533 | 3.4767 | 4.3433 | 5.4867 | 6.3133 | 6.9867 | 7.2433 | 7.3933 | 7.2733 | 6.6867 | 5.9233 | 5.2767 | 4.6333 | 4.2267 | 4.1533 | 4.08 | 3.8033 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7333 | 50.8667 | 146.3333 | 217.2667 | 286.4333 | 319 | 301.6 | 249.0333 | 160.8 | 70.1 | 12.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1337 | 3.9027 | 200.1593 | 1.1467 | 138.9677 | 1.0615 | 55.5871 | 0.79611 | 196.4124 | 0.70753 | 0.0054044 | 0.28301 | 0.0040533
|  | Equivalent full-load hours | 24 | 9 | 15 | [7 empty] | Dec | 2.6784 | 744 | 31 |  | NOx | 2.5064e-05 | 0.00017029 | kg/kWh NG |  |  |  | Dec | 0.71743 | 0.95657 | 0.28697 | 0.71743 |  | Dec | -3.677 | 4.2945 | 115.8563 | 82.5397 | 39.0707 | 19.7786 | 19.2697 | 21.3629 | 49.0963 | 95.2773 | 62.5826 | -4.8935 | -4.7839 | -4.9387 | -5.2387 | -5.2968 | -5.6452 | -5.6935 | -5.3516 | -4.4806 | -3.2129 | -2.1 | -1.4935 | -0.91935 | -0.70323 | -0.68387 | -1.471 | -2.4742 | -3.3129 | -3.6774 | -4.0226 | -4.1548 | -4.3677 | -4.5484 | -4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2258 | 98.7097 | 182.5806 | 252.129 | 262 | 262.4839 | 213.2903 | 143.871 | 59.7419 | 6.9677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.2685 | -4.5199 | 166.3369 | 0.46452 | 119.3349 | 0.44434 | 47.7339 | 0.33326 | 167.8464 | 0.71098 | 0.0026473 | 0.28439 | 0.0019855
|  | Total hours | 168 | 45 | 60 | 18 | 45 | 63 |  |  |  |  | Total | 31.536 | 8760 | 365 |  | SOx | 0.0018655 | 9.6622e-07 | kg/kWh NG | bar: Monthly Ave Temps for Each Hour 1 to Monthly Ave Temps for Each Hour 24
|  | Fraction |  | 26.79% | 35.71% | 10.71% | 26.79% | 37.5% | [34 empty] | Monthly Ave Temps for Each Hour 24: Occ; Monthly avg horizontal radiation for each hour 1: 0; Monthly avg horizontal radiation for each hour 2: 0; Monthly avg horizontal radiation for each hour 3: 0; Monthly avg horizontal radiation for each hour 4: 0; Monthly avg horizontal radiation for each hour 5: 0; Monthly avg horizontal radiation for each hour 6: 0; Monthly avg horizontal radiation for each hour 7: 0; Monthly avg horizontal radiation for each hour 8: 1; Monthly avg horizontal radiation for each hour 9: 1; Monthly avg horizontal radiation for each hour 10: 1; Monthly avg horizontal radiation for each hour 11: 1; Monthly avg horizontal radiation for each hour 12: 1; Monthly avg horizontal radiation for each hour 13: 1; Monthly avg horizontal radiation for each hour 14: 1; Monthly avg horizontal radiation for each hour 15: 1; Monthly avg horizontal radiation for each hour 16: 1; Monthly avg horizontal radiation for each hour 17: 0; Monthly avg horizontal radiation for each hour 18: 0; Monthly avg horizontal radiation for each hour 19: 0; Monthly avg horizontal radiation for each hour 20: 0; Monthly avg horizontal radiation for each hour 21: 0; Monthly avg horizontal radiation for each hour 22: 0; Monthly avg horizontal radiation for each hour 23: 0; Monthly avg horizontal radiation for each hour 24: 0
|  | Occupancy fraction |  | 100% | 11.11% | 11.11% | 11.11% | 11.11% | [34 empty] | Monthly Ave Temps for Each Hour 24: Unocc; Monthly avg horizontal radiation for each hour 1: 1; Monthly avg horizontal radiation for each hour 2: 1; Monthly avg horizontal radiation for each hour 3: 1; Monthly avg horizontal radiation for each hour 4: 1; Monthly avg horizontal radiation for each hour 5: 1; Monthly avg horizontal radiation for each hour 6: 1; Monthly avg horizontal radiation for each hour 7: 1; Monthly avg horizontal radiation for each hour 8: 0; Monthly avg horizontal radiation for each hour 9: 0; Monthly avg horizontal radiation for each hour 10: 0; Monthly avg horizontal radiation for each hour 11: 0; Monthly avg horizontal radiation for each hour 12: 0; Monthly avg horizontal radiation for each hour 13: 0; Monthly avg horizontal radiation for each hour 14: 0; Monthly avg horizontal radiation for each hour 15: 0; Monthly avg horizontal radiation for each hour 16: 0; Monthly avg horizontal radiation for each hour 17: 1; Monthly avg horizontal radiation for each hour 18: 1; Monthly avg horizontal radiation for each hour 19: 1; Monthly avg horizontal radiation for each hour 20: 1; Monthly avg horizontal radiation for each hour 21: 1; Monthly avg horizontal radiation for each hour 22: 1; Monthly avg horizontal radiation for each hour 23: 1; Monthly avg horizontal radiation for each hour 24: 1
[12 empty] | m2 --> ft2 | 10.7639
|  | Operation Ratio | 3.6058 | [8 empty] | mBTU --> kWh | 293
|  | fop_school | 1.2085 | fop_school=0.08 * operation ratio + 0.92 (developed by parametric study on the basis of standardized model) | [7 empty] | kWh --> MJ | 3.6101
[12 empty] | kWh --> kBTU | 3.4121
[12 empty] | CFM --> m3/hr | 1.699
[12 empty] | CFM --> m3/s | 0.000471
[12 empty] | CFM-->l/s | 0.471
[12 empty] | m3/hr-->liter/s | 0.278
[12 empty] | gallon --> g | 3.54
Lighting Energy | [5 empty] | Dropdown menu |  |  | W_t=W_L,t+W_P,t |  |  |  | W_L,t = {(P_n*F_c)*[(t_D*F_O*F_D)+(t_N*F_O)]}/1000 [kWh]
|  | P_n: installed lighting power (W/m2) | 7.18 |  |  | Daylighting factor |  |  | W_t | total lighting energy (kWh) |  |  | P_n | total installed lighting power in the room or zone
|  | W_pc:Parasitic lighting energy (kWh/m2/yr | 6 |  |  | Manual | 1 |  | W_L | illumination energy (kWh) |  |  | F_c | constant illuminance control factor
|  |  | #REF! |  |  | Photo cell dimming-with daylighting sensing | 0.8 |  | W_P | parasitic energy (kWh) |  |  | F_D | daylight dependency factor
|  | F_D: Daylight dependency factor | 1 |  |  | Occupancy dependency factor | [6 empty] | F_O | occupancy factor
|  |  | #REF! |  |  | Manual | 1 | [5 empty] | t_D | operating hours during daylighting time
|  | F_O: Occupancy factor | 1 |  |  | Automatic >=60% of the connected load | 0.8 | [5 empty] | t_N | operating hours during non-daylighting hours
|  |  | #REF! |  |  | Constant control system
|  | F_c: Constant illuminance control factor | 1 |  |  | No constant illumination control | 1
[6 empty] | Constant illumination control | 0.9
|  | t_D: Operating hours during daylighting time | 2700
|  | t_N: Operating hours during non-daylighting hours | 0
|  |  | Illumination (kWh) | Parasitic (kWh) | Total Lighting (kWh) |  | Illumination (MJ) | Parasitic (MJ) | Total Lighting (MJ) |  | Exterior Lighting
|  | Total [kwh] | 133201.206 | 41226 | 174427.206 | [9 empty] | On hours | Eext_light [kWh/m2]
|  | Jan | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  | Installed power [W] | 1131 | Jan | 341 | 0.05613
|  | Feb | 10218.1747 | 3162.5425 | 13380.7172 |  | 36888.7174 | 11417.1208 | 48305.8382 |  |  | Average fraction of light on per day | 0.45833 | Feb | 308 | 0.050698
|  | Mar | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | Mar | 341 | 0.05613
|  | Apr | 10948.0443 | 3388.4384 | 14336.4827 |  | 39523.6257 | 12232.6294 | 51756.2552 |  |  |  |  | Apr | 330 | 0.05432
|  | May | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | May | 341 | 0.05613
|  | Jun | 10948.0443 | 3388.4384 | 14336.4827 |  | 39523.6257 | 12232.6294 | 51756.2552 |  |  |  |  | Jun | 330 | 0.05432
|  | Jul | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | Jul | 341 | 0.05613
|  | Aug | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | Aug | 341 | 0.05613
|  | Sep | 10948.0443 | 3388.4384 | 14336.4827 |  | 39523.6257 | 12232.6294 | 51756.2552 |  |  |  |  | Sep | 330 | 0.05432
|  | Oct | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | Oct | 341 | 0.05613
|  | Nov | 10948.0443 | 3388.4384 | 14336.4827 |  | 39523.6257 | 12232.6294 | 51756.2552 |  |  |  |  | Nov | 330 | 0.05432
|  | Dec | 11312.9791 | 3501.3863 | 14814.3654 |  | 40841.0799 | 12640.3838 | 53481.4637 |  |  |  |  | Dec | 341 | 0.05613
[14 empty] | Total | 4015 | 0.66089
Envelope
Envelope
|  | Area | S | SE | E | NE | N | NW | W | SW | Roof
|  | Opaque Area | 603.2 | 0 | 213.2 | 0 | 603.2 | 0 | 213.2 | 0 | 6871 | 8503.8
|  | Window Type 1 | 324.8 | 0 | 114.8 | 0 | 324.8 | 0 | 115 | 0 | 0
Window2 Type2
|  | U-value | S | SE | E | NE | N | NW | W | SW | Hor
|  | Opaque | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
|  | Window Type 1 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
Window2 Type2
|  | Htr | S | SE | E | NE | N | NW | W | SW | Hor
|  | Opaque_Ht | 218.9616 | 0 | 77.3916 | 0 | 218.9616 | 0 | 77.3916 | 0 | 1855.17
|  | Window1 _Ht | 861.6944 | 0 | 304.5644 | 0 | 861.6944 | 0 | 305.095 | 0 | 0
Window2 _Ht
|  | Total_Ht | 1080.656 | 0 | 381.956 | 0 | 1080.656 | 0 | 382.4866 | 0 | 1855.17
|  | Solar Transmittance | S | SE | E | NE | N | NW | W | SW | Hor
Window 1 SHGC
|  | Window 1 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Window 2
Window1 SCF | bar: S to Hor
|  | % of SCF | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Window2 SCF
|  | % of SCF | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Window1 SDF | bar: S to Hor
|  | % of SDF | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Window2 SDF
|  | % of SDF | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Opaque Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  | Window1 Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
|  | Window2 Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84
Dropdown menu
[Table] Shading Reduction Factor (Blind Control)
<Source: NEN 2916 Table 11>
[5 empty] | Shading system | Redcution factor
|  | Am factor | S: Don't use Am factor in monthly spreadsheet; E: User-moveable; NE: 0.5
|  | Ht Coefficient | S: 4780.9246; E: Automatic control; NE: 0.35
[5 empty] | All other cases | 1
|  |  | S | SE | E | NE | N | NW | W | SW | HOR
|  | Window1 Area | 324.8 | 0 | 114.8 | 0 | 324.8 | 0 | 115 | 0 | 0 |  |  | Window2 Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Opaque Area | 603.2 | 0 | 213.2 | 0 | 603.2 | 0 | 213.2 | 0 | 6871
|  | U-value | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0 |  |  | U-value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
|  | Shading correction factor | [11 empty] | Shading correction factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: S to HOR
|  | SCF % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  | SCF % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Shading device factor | [11 empty] | Shading device factor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | bar: S to HOR
|  | SDF % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  |  | SDF % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
|  | Form Factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | Form Factor | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | Form Factor(is the form factor between the element and the sky (1 for an unshaded horizontal roof, 0,5 for an unshaded vertical wall) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1
|  | Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  |  | Emissivity | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 |  |  | Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  | hr =5ε | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  | hr =5ε | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |  |  | hr (hr =5ε) External radiative heat transfer coefficient | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  | αS,c | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | dimensionless absorption coefficient for solar radiation of the opaque part |  | αS,c | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | 0.84 | dimensionless absorption coefficient for solar radiation of the opaque part |  | αS,c | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | dimensionless absorption coefficient for solar radiation of the opaque part
|  | Rse | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | external surface heat resistance of the element |  | Rse | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | external surface heat resistance of the element |  | Rse | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | 0.043478 | external surface heat resistance of the element
|  | Δθer | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | the average difference between the external air temperature and the apparent sky temperature, in °C; |  | Δθer | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | the average difference between the external air temperature and the apparent sky temperature, in °C; |  | Δθer | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | the average difference between the external air temperature and the apparent sky temperature, in °C;
|  | g⊥ | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0 |  |  | g⊥ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | gg | 0.3834 | 0.3834 | 0.3834 | 0.3834 | 0.3834 | 0.3834 | 0.3834 | 0.3834 | 0 | Total solar energy transmittance of the transparent part of the element |  | gg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total solar energy transmittance of the transparent part of the element
|  | FF | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | Frame factor |  | FF | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | Frame factor
|  | Effective Solar Collecting Area (m2) | [12 empty] | Effective Solar Collecting Area (m2) | [18 empty] | Effective Opaque Solar Collecting Area (m2)
|  | As,t = Fsh,g gg (1-FF)Aw,p | [12 empty] | As,t = Fsh,g gg (1-FF)Aw,p | [18 empty] | Asol=αS,c * Rse * Uc * Ac
|  |  | S | SE | E | NE | N | NW | W | SW | HOR |  |  |  | SW | S | SE | E | NE | N | NW | W | HOR | Total |  |  | S | SE | E | NE | N | NW | W | SW | HOR
|  |  | 93.3962 | 0 | 33.0107 | 0 | 93.3962 | 0 | 33.0683 | 0 | 0 |  |  | For heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 6.664 | 0 | 2.3554 | 0 | 6.664 | 0 | 2.3554 | 0 | 56.4617
Thermal Radiation to the sky (W)
Φr = Rse×Uc×Ac×hr×Δθer
[27 empty] | S | SE | E | NE | N | NW | W | SW | HOR | Total
[27 empty] | 471.2434 | 0 | 166.5602 | 0 | 471.2434 | 0 | 166.5602 | 0 | 3992.6485 | 5268.2557
|  | Solar Heat Gain (MJ) | [35 empty] | Solar Gain (MJ)
[27 empty] | Φr = Rse×Uc×Ac×hr×Δθer S: Φsol,k=Fsh,ob,kAsol,kIsol,k−Fr,kΦr,k |  | Qs = ΣQs,c + Σ(1-bj)Qs,u,j
|  | Window1 (MJ) | S | SE | E | NE | N | NW | W | SW | HOR | Total |  | Window2 (MJ) | SW | S | SE | E | NE | N | NW | W | HOR | Total |  | Opaque (MJ) | S | SE | E | NE | N | NW | W | SW | HOR | Total |  | Qs,c = Σ[Is,k * Fs,o,k * As,k]-Fr,k*Qr,k
|  | Jan | 31343.7935 | 0 | 3804.1195 | 0 | 5756.75 | 0 | 5209.5191 | 0 | 0 | 46114.1821 |  | Jan | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Jan | 1605.3666 | 0 | 48.3758 | 0 | -220.3311 | 0 | 148.008 | 0 | 436.0316 | 2017.4508 |  | 48131.633
|  | Feb | 32373.1555 | 0 | 4826.7889 | 0 | 7252.4945 | 0 | 6359.843 | 0 | 0 | 50812.2819 |  | Feb | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Feb | 1739.8872 | 0 | 142.9319 | 0 | -52.533 | 0 | 251.5299 | 0 | 4531.5254 | 6613.3414 |  | 57425.6234
|  | Mar | 36573.6857 | 0 | 7493.6463 | 0 | 10712.4482 | 0 | 8853.085 | 0 | 0 | 63632.8652 |  | Mar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Mar | 1978.5321 | 0 | 311.6325 | 0 | 133.27 | 0 | 407.5331 | 0 | 10982.9774 | 13813.9452 |  | 77446.8104
|  | Apr | 31360.8234 | 0 | 8976.6881 | 0 | 13102.3795 | 0 | 10683.6885 | 0 | 0 | 64123.5795 |  | Apr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Apr | 1626.9395 | 0 | 424.6465 | 0 | 324.1551 | 0 | 545.1194 | 0 | 16445.8788 | 19366.7393 |  | 83490.3187
|  | May | 33066.5489 | 0 | 12196.8193 | 0 | 19151.804 | 0 | 14068.8328 | 0 | 0 | 78484.0051 |  | May | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | May | 1728.2894 | 0 | 647.2153 | 0 | 735.4385 | 0 | 779.0422 | 0 | 26960.8017 | 30850.7871 |  | 109334.7922
|  | Jun | 29311.3265 | 0 | 12670.6511 | 0 | 21295.6521 | 0 | 14121.7666 | 0 | 0 | 77399.3963 |  | Jun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Jun | 1480.7029 | 0 | 688.2198 | 0 | 908.765 | 0 | 790.008 | 0 | 28027.9568 | 31895.6524 |  | 109295.0487
|  | Jul | 32552.1771 | 0 | 12441.8428 | 0 | 21277.8643 | 0 | 14715.6792 | 0 | 0 | 80987.5633 |  | Jul | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Jul | 1691.5877 | 0 | 664.6983 | 0 | 887.1381 | 0 | 825.116 | 0 | 28226.7181 | 32295.2582 |  | 113282.8215
|  | Aug | 34044.4401 | 0 | 10940.9523 | 0 | 16574.1858 | 0 | 12697.7716 | 0 | 0 | 74257.3498 |  | Aug | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Aug | 1798.0643 | 0 | 557.6061 | 0 | 551.5192 | 0 | 681.3838 | 0 | 21828.8401 | 25417.4135 |  | 99674.7633
|  | Sep | 37112.6388 | 0 | 8813.906 | 0 | 11579.9181 | 0 | 10191.0218 | 0 | 0 | 67697.4847 |  | Sep | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Sep | 2037.3455 | 0 | 413.0316 | 0 | 215.5238 | 0 | 510.0276 | 0 | 15217.1594 | 18393.0878 |  | 86090.5725
|  | Oct | 38290.7235 | 0 | 6558.1206 | 0 | 8643.2431 | 0 | 7774.7503 | 0 | 0 | 61266.8376 |  | Oct | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Oct | 2101.047 | 0 | 244.8804 | 0 | -14.3728 | 0 | 330.7252 | 0 | 7838.9192 | 10501.1989 |  | 71768.0365
|  | Nov | 27815.9794 | 0 | 3871.8976 | 0 | 6202.4617 | 0 | 4777.4064 | 0 | 0 | 42667.7452 |  | Nov | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Nov | 1374.0062 | 0 | 60.4073 | 0 | -168.1708 | 0 | 124.4247 | 0 | 740.8323 | 2131.4998 |  | 44799.245
|  | Dec | 28981.7302 | 0 | 3454.4749 | 0 | 4820.3716 | 0 | 4348.4627 | 0 | 0 | 41605.0394 |  | Dec | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Dec | 1436.8277 | 0 | 23.4278 | 0 | -287.144 | 0 | 86.6764 | 0 | -1229.738 | 30.0498 |  | 41635.0893
|  | Total | 392827.0225 | 0 | 96049.9075 | 0 | 146369.5731 | 0 | 113801.8271 | 0 | 0 | 749048.3302 |  | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Total | 20598.5961 | 0 | 4227.0734 | 0 | 3013.2581 | 0 | 5479.5942 | 0 | 160007.9026 | 193326.4243 |  | 942374.7545
Thermal Radiation to the sky (not applied for the glazing area)
Φr = Rse×Uc×Ac×hr×Δθer
[15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Gains and Losses
Internal heat gain
|  |  | occupied | Unoccupied | averaged | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night | Internal Heat Gain (MJ) | ΦI
|  | Occupants (W/m2) | 19.2308 | 0.83916 | 5.7655 | 2.1367 | 2.1367 | 2.1367 | ΦI,OCC (W) | 39614.6441
|  | Appliances (W/m2) | 13.96 | 3.77 | 6.4995 | 1.5511 | 1.5511 | 1.5511 | ΦI,APP (W) | 44657.8191
|  | Lighting (W/m2) | 8.2987 |  | 2.8979 | 0.92207 | 0.92207 | 0.92207 | ΦI,LI (W) | 19911.7815
|  | Total Internal Heat flow (W/m2) | 41.4894 |  | 41.4894 | 4.6099 | 4.6099 | 4.6099 | ΦI Total | 104184.2447
| Heat gains | Internal heat gain (MJ) | NE: Solar heat gain (MJ); SW: Total in MJ/m2
|  | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night |  | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night |  | Unoccupied Weekday night | Unoccupied Weekend daytime | Unoccupied Weekend night
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 353.5864 | 13575.1019 | 265.1898 |  | 32044.2125 | 78979.2893 | 32044.2125
|  | 27366.8313 | 8210.0494 | 20525.1235 |  | 1030.3047 | 15892.1686 | 772.7286 |  | 32867.0556 | 92986.9521 | 32867.0556
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 2496.9221 | 20879.199 | 1872.6916 |  | 34284.8562 | 104431.6388 | 34284.8562
|  | 29321.6049 | 8796.4815 | 21991.2037 |  | 4748.292 | 21480.2308 | 3561.219 |  | 36803.901 | 109021.0832 | 36803.901
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 7725.4831 | 27375.7705 | 5794.1123 |  | 39750.7951 | 127070.03 | 39750.7951
|  | 29321.6049 | 8796.4815 | 21991.2037 |  | 9102.9382 | 26675.6877 | 6827.2037 |  | 41507.9942 | 127729.0041 | 41507.9942
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 8866.4793 | 27933.2808 | 6649.8595 |  | 40943.5928 | 129012.7679 | 40943.5928
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 6240.9081 | 25358.0498 | 4680.6811 |  | 38198.82 | 120038.9441 | 38198.82
|  | 29321.6049 | 8796.4815 | 21991.2037 |  | 3412.1261 | 22891.2434 | 2559.0945 |  | 35360.5119 | 114101.89 | 35360.5119
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 1204.9816 | 19902.6625 | 903.7362 |  | 32934.2613 | 101028.7336 | 32934.2613
|  | 29321.6049 | 8796.4815 | 21991.2037 |  | 242.1118 | 12678.7284 | 181.5838 |  | 31936.1137 | 77328.4306 | 31936.1137
|  | 30298.9918 | 9089.6975 | 22724.2438 |  | 110.2213 | 11840.6291 | 82.666 |  | 31789.7986 | 72935.2283 | 31789.7986
| Hve (Ventilation loss) | To be added…
Temperature (Occ, Weekday Unocc, Weekend) |  |  | Total: [Table]Envelope Heat Capacity Class
<Source: ISO 13790 12.3>
| Temperature setpoint | Heating Setpoint (°C ) | 20.6 | 16.4 | Reduced set-point temperature or switch off | 1 |  |  | Internal Heat Capacity (J/(Km2)) | 98010 |  | Category Max | Class | Seasonal, Monthly, Hourly Cm | Am factor | Class
|  | Cooling Setpoint (°C ) | 24.2 | 26.3 | Reduced set-point temperature or switch off | 1 |  |  | Internal HC (J) | 673426710 |  | 0 |  | 0 | 2.5
|  |  | W: Envelope Heat Capacity (J/K/m2); SW: 28921 | Very Light: 80,000 J/(Km2) | 80000 | 2.5 | *Af
|  |  | W: Envelope Heat Capacity (J/K/m2); SW: 245938399.8 | Light : 110,000 J/(Km2) | 110000 | 2.5 | *Af
| Unoccupied Parameter | Htr (W/K) | S: 4780.9246 | Medium: 165,000 J/(Km2) | 165000 | 2.5 | *Af
|  | Hve (W/K) | S: 0 | Heavy: 260,000 J/(Km2) | 260000 | 3 | *Af
|  | Htotal (W/K) | S: 4780.9246 | Very heavy: 370,000 J/(Km2) | 370000 | 3.5 | *Af
|  | M (Wh/K) | S: 255379.1972
θ_unocc (t)=(θ_(int,set)-θ_(e,unocc)-Q_(gn,unocc)/H_unocc ) e^(-H_unocc/M t)+θ_(e,unocc)+Q_(gn,unocc)/H_unocc
θ_(cal,unocc) (t)=M/(t〖∙H〗_unocc ) (θ_(int,set)-θ_(e,unocc)-Q_(gn,unocc)/H_unocc )(1-e^(-H_unocc/M∙t) )+θ_(e,unocc)+Q_(gn,unocc)/H_unocc
|  |  | Occupied Heating Set-point Temperature |  | 9 | 15 | 9 | 15 | 9 | 15
|  |  | T_i_heat_occ |  | T_i_heat_occ | T_i_SatMor_heat | T_i_SatAft_heat | T_i_SunMor_heat | T_i_SunAft_heat | T_i_MonMor_heat |  | T_i_FriNight_heat_avg | T_i_SatDay_heat_avg | T_i_SatNight_heat_avg | T_i_SunDay_heat_avg | T_i_SunNight_heat_avg
|  | Jan | 20.6 |  | 20.6 | 15.8665 | 15.4513 | 11.9784 | 12.1661 | 9.4975 |  | 18.1226 | 16.1441 | 14.4608 | 16.1441 | 14.4608
|  | Feb | 20.6 |  | 20.6 | 16.4099 | 16.7112 | 13.4732 | 14.2299 | 11.5994 |  | 18.407 | 16.5648 | 15.0166 | 16.5557 | 14.7452
|  | Mar | 20.6 |  | 20.6 | 17.9453 | 19.4631 | 17.0868 | 18.7376 | 16.5389 |  | 19.2106 | 18.7255 | 18.2194 | 17.9354 | 17.5869
|  | Apr | 20.6 |  | 20.6 | 19.6011 | 21.9273 | 20.6034 | 22.7742 | 21.243 |  | 20.0772 | 20.7968 | 21.2344 | 21.7193 | 21.9728
|  | May | 20.6 |  | 20.6 | 20.7375 | 24.6483 | 23.7947 | 27.2315 | 25.7454 |  | 20.672 | 22.7478 | 24.2015 | 25.5613 | 26.4537
|  | Jun | 20.6 |  | 20.6 | 22.3965 | 26.8188 | 27.0927 | 30.7869 | 30.0893 |  | 21.5402 | 24.6697 | 26.9622 | 28.9917 | 30.4218
|  | Jul | 20.6 |  | 20.6 | 23.1369 | 27.9226 | 28.6667 | 32.5949 | 32.1951 |  | 21.9278 | 25.5969 | 28.312 | 30.6859 | 32.3857
|  | Aug | 20.6 |  | 20.6 | 22.4142 | 26.664 | 26.9935 | 30.5333 | 29.9155 |  | 21.5495 | 24.5987 | 26.8365 | 28.8131 | 30.21
|  | Sep | 20.6 |  | 20.6 | 21.3319 | 25.0416 | 24.6861 | 27.8756 | 26.8262 |  | 20.9831 | 23.2388 | 24.8555 | 26.3256 | 27.3264
|  | Oct | 20.6 |  | 20.6 | 19.5094 | 21.9101 | 20.4988 | 22.7461 | 21.1301 |  | 20.0292 | 20.7435 | 21.1715 | 21.654 | 21.9003
|  | Nov | 20.6 |  | 20.6 | 18.1474 | 18.7926 | 16.7825 | 17.6393 | 15.9116 |  | 19.3164 | 18.4791 | 17.7406 | 17.2229 | 16.7351
|  | Dec | 20.6 |  | 20.6 | 16.0778 | 15.5986 | 12.3009 | 12.4073 | 9.891 |  | 18.2332 | 16.128 | 14.5714 | 16.128 | 14.5714 |  |  |  | Weekday Unoccupied Night Average | Weekend Unoccupied Average Temperature |  | Average Temperature |  | Heating Internal Temperature
[18 empty] | T_i_weekend_heat_avg |  | T_i_unocc_weekday_night | T_i_unocc_weekend |  | T_i_average |  | T_i_heat_average_cal
[5 empty] | 20.6 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 |  | 18.1226 | 16.4 | 16.4 | 16.4 | 16.4 |  | 16.7445 |  | 18.1226 | 16.7445 |  | 18.2694 |  | 18.2694
[5 empty] | 20.6 | 16.4099 | 16.7112 | 16.4 | 16.4 | 16.4 |  | 18.407 | 16.5648 | 16.4 | 16.5557 | 16.4 |  | 16.8655 |  | 18.407 | 16.8655 |  | 18.4164 |  | 18.4164
[5 empty] | 20.6 | 17.9453 | 19.4631 | 17.0868 | 18.7376 | 16.5389 |  | 19.2106 | 18.7255 | 18.2194 | 17.9354 | 17.5869 |  | 18.3356 |  | 19.2106 | 18.3356 |  | 19.2546 |  | 19.2546
[5 empty] | 20.6 | 19.6011 | 21.9273 | 20.6034 | 22.7742 | 21.243 |  | 20.0772 | 20.7968 | 21.2344 | 21.7193 | 21.9728 |  | 21.1601 |  | 20.0772 | 21.1601 |  | 20.6233 |  | 20.6
[5 empty] | 20.6 | 20.7375 | 24.6483 | 23.7947 | 27.2315 | 25.7454 |  | 20.672 | 22.7478 | 24.2015 | 25.5613 | 26.4537 |  | 23.9273 |  | 20.672 | 23.9273 |  | 21.8734 |  | 20.6
[5 empty] | 20.6 | 22.3965 | 26.8188 | 27.0927 | 30.7869 | 30.0893 |  | 21.5402 | 24.6697 | 26.9622 | 28.9917 | 30.4218 |  | 26.5171 |  | 21.5402 | 26.5171 |  | 23.1547 |  | 20.6
[5 empty] | 20.6 | 23.1369 | 27.9226 | 28.6667 | 32.5949 | 32.1951 |  | 21.9278 | 25.5969 | 28.312 | 30.6859 | 32.3857 |  | 27.7817 |  | 21.9278 | 27.7817 |  | 23.7673 |  | 20.6
[5 empty] | 20.6 | 22.4142 | 26.664 | 26.9935 | 30.5333 | 29.9155 |  | 21.5495 | 24.5987 | 26.8365 | 28.8131 | 30.21 |  | 26.4015 |  | 21.5495 | 26.4015 |  | 23.1147 |  | 20.6
[5 empty] | 20.6 | 21.3319 | 25.0416 | 24.6861 | 27.8756 | 26.8262 |  | 20.9831 | 23.2388 | 24.8555 | 26.3256 | 27.3264 |  | 24.5459 |  | 20.9831 | 24.5459 |  | 22.2165 |  | 20.6
[5 empty] | 20.6 | 19.5094 | 21.9101 | 20.4988 | 22.7461 | 21.1301 |  | 20.0292 | 20.7435 | 21.1715 | 21.654 | 21.9003 |  | 21.0997 |  | 20.0292 | 21.0997 |  | 20.5835 |  | 20.5835
[5 empty] | 20.6 | 18.1474 | 18.7926 | 16.7825 | 17.6393 | 16.4 |  | 19.3164 | 18.4791 | 17.7406 | 17.2229 | 16.7351 |  | 17.8988 |  | 19.3164 | 17.8988 |  | 19.1286 |  | 19.1286
[5 empty] | 20.6 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 |  | 18.2332 | 16.4 | 16.4 | 16.4 | 16.4 |  | 16.7666 |  | 18.2332 | 16.7666 |  | 18.3172 |  | 18.3172
Occupied Cooling Set-point Temperature
|  |  | T_i_cool_occ |  | T_i_cool_occ | T_i_SatMor_cool | T_i_SatAft_cool | T_i_SunMor_cool | T_i_SunAft_cool | T_i_MonMor_cool |  | T_i_FriNight_cool_avg | T_i_SatDay_cool_avg | T_i_SatNight_cool_avg | T_i_SunDay_cool_avg | T_i_SunNight_cool_avg
|  | Jan | 24.2 |  | 24.2 | 18.5852 | 17.7484 | 13.7131 | 13.6318 | 10.6044 |  | 21.2614 | 18.155 | 15.6365 | 13.6713 | 12.0474
|  | Feb | 24.2 |  | 24.2 | 19.1285 | 19.0083 | 15.2079 | 15.6956 | 12.7063 |  | 21.5457 | 19.0667 | 17.0193 | 15.4586 | 14.1311
|  | Mar | 24.2 |  | 24.2 | 20.664 | 21.7601 | 18.8214 | 20.2033 | 17.6458 |  | 22.3493 | 21.2274 | 20.2221 | 19.5318 | 18.8648
|  | Apr | 24.2 |  | 24.2 | 22.3197 | 24.2243 | 22.3381 | 24.2399 | 22.3498 |  | 23.2159 | 23.2988 | 23.2371 | 23.3157 | 23.2507
|  | May | 24.2 |  | 24.2 | 23.4561 | 26.9454 | 25.5293 | 28.6972 | 26.8522 |  | 23.8107 | 25.2497 | 25.6416 | 27.1577 | 25.6416
|  | Jun | 24.2 |  | 24.2 | 25.1151 | 29.1159 | 28.8274 | 32.2526 | 31.1961 |  | 24.6789 | 27.1716 | 26.5098 | 28.2621 | 26.5098
|  | Jul | 24.2 |  | 24.2 | 25.8555 | 30.2196 | 30.4014 | 34.0606 | 33.302 |  | 25.0665 | 28.0988 | 26.8974 | 28.5079 | 26.8974
|  | Aug | 24.2 |  | 24.2 | 25.1328 | 28.9611 | 28.7282 | 31.999 | 31.0223 |  | 24.6882 | 27.1006 | 26.5191 | 28.1748 | 26.5191
|  | Sep | 24.2 |  | 24.2 | 24.0505 | 27.3386 | 26.4207 | 29.3413 | 27.9331 |  | 24.1218 | 25.7407 | 25.9527 | 27.8109 | 25.9527
|  | Oct | 24.2 |  | 24.2 | 22.2281 | 24.2072 | 22.2335 | 24.2118 | 22.2369 |  | 23.1679 | 23.2454 | 23.1742 | 23.2504 | 23.1782
|  | Nov | 24.2 |  | 24.2 | 20.866 | 21.0896 | 18.5172 | 19.105 | 17.0184 |  | 22.4551 | 20.981 | 19.7433 | 18.8193 | 18.013
|  | Dec | 24.2 |  | 24.2 | 18.7964 | 17.8956 | 14.0356 | 13.873 | 10.9978 |  | 21.3719 | 18.3334 | 15.8754 | 13.952 | 12.3682 |  |  |  | Weekday Unoccupied Night Average | Weekend Unoccupied Average Temperature |  |  |  | Cooling Internal Temperature
[18 empty] | T_i_weekend_cool_avg |  | T_i_unocc_weekday_night | T_i_unocc_weekend |  | T_i_average |  | T_i_cool_average_cal
[5 empty] | 24.2 | 18.5852 | 17.7484 | 13.7131 | 13.6318 | 10.6044 |  | 21.2614 | 18.155 | 15.6365 | 13.6713 | 12.0474 |  | 16.1543 |  | 21.2614 | 16.1543 |  | 20.1333 |  | 24.2
[5 empty] | 24.2 | 19.1285 | 19.0083 | 15.2079 | 15.6956 | 12.7063 |  | 21.5457 | 19.0667 | 17.0193 | 15.4586 | 14.1311 |  | 17.4443 |  | 21.5457 | 17.4443 |  | 20.7187 |  | 24.2
[5 empty] | 24.2 | 20.664 | 21.7601 | 18.8214 | 20.2033 | 17.6458 |  | 22.3493 | 21.2274 | 20.2221 | 19.5318 | 18.8648 |  | 20.4391 |  | 22.3493 | 20.4391 |  | 22.1287 |  | 24.2
[5 empty] | 24.2 | 22.3197 | 24.2243 | 22.3381 | 24.2399 | 22.3498 |  | 23.2159 | 23.2988 | 23.2371 | 23.3157 | 23.2507 |  | 23.2636 |  | 23.2159 | 23.2636 |  | 23.4974 |  | 24.2
[5 empty] | 24.2 | 23.4561 | 26.3 | 25.5293 | 26.3 | 26.3 |  | 23.8107 | 25.2497 | 25.6416 | 26.3 | 25.6416 |  | 25.3287 |  | 23.8107 | 25.3287 |  | 24.4842 |  | 24.4842
[5 empty] | 24.2 | 25.1151 | 26.3 | 26.3 | 26.3 | 26.3 |  | 24.6789 | 26.3 | 26.3 | 26.3 | 26.3 |  | 25.9758 |  | 24.6789 | 25.9758 |  | 25.037 |  | 25.037
[5 empty] | 24.2 | 25.8555 | 26.3 | 26.3 | 26.3 | 26.3 |  | 25.0665 | 26.3 | 26.3 | 26.3 | 26.3 |  | 26.0533 |  | 25.0665 | 26.0533 |  | 25.2044 |  | 25.2044
[5 empty] | 24.2 | 25.1328 | 26.3 | 26.3 | 26.3 | 26.3 |  | 24.6882 | 26.3 | 26.3 | 26.3 | 26.3 |  | 25.9776 |  | 24.6882 | 25.9776 |  | 25.041 |  | 25.041
[5 empty] | 24.2 | 24.0505 | 26.3 | 26.3 | 26.3 | 26.3 |  | 24.1218 | 25.7407 | 25.9527 | 26.3 | 25.9527 |  | 25.6136 |  | 24.1218 | 25.6136 |  | 24.7022 |  | 24.7022
[5 empty] | 24.2 | 22.2281 | 24.2072 | 22.2335 | 24.2118 | 22.2369 |  | 23.1679 | 23.2454 | 23.1742 | 23.2504 | 23.1782 |  | 23.2032 |  | 23.1679 | 23.2032 |  | 23.4576 |  | 24.2
[5 empty] | 24.2 | 20.866 | 21.0896 | 18.5172 | 19.105 | 17.0184 |  | 22.4551 | 20.981 | 19.7433 | 18.8193 | 18.013 |  | 20.0023 |  | 22.4551 | 20.0023 |  | 22.0027 |  | 24.2
[5 empty] | 24.2 | 18.7964 | 17.8956 | 14.0356 | 13.873 | 10.9978 |  | 21.3719 | 18.3334 | 15.8754 | 13.952 | 12.3682 |  | 16.3802 |  | 21.3719 | 16.3802 |  | 20.2575 |  | 24.2
Ventilation and Fan |  |  | W: MAX(0.0146*$D$303*(0.7*$D$304*ABS(AG5-Z231))^0.667,0.001)
22.9144
|  | Ventilation Zone Height (m) | S: 4
|  |  | E: Heating |  |  |  |  | Exposed façade
|  | Total occupants | 1101.1218 |  |  | qv,me | qv,me (for calculation) |  | qv,stack (m3/h/m2) | qv,wind (m3/h/m2) | qv-sw (m3/h/m2) | qv,inf (m3/h/m2) |  | qv,tot (m3/h/m2) | Hve (W/K/m2) |  | More than one exposed façade |  | EN ISO 13789 Table C.2 | [7 empty] | Dropdown menu
|  | Vent type | 1 |  | Jan | 0.49508 | 0.13261 |  | 0.25756 | 0.49822 | 0.51457 | 0.51457 |  | 0.64718 | 0.21573 |  | Only one exposed façade |  | Shieding class | Multi family building air change rate | [6 empty] | [Table] Heat recovery system efficiency
| Minimum ventilation for Non-Res | Vmin: Non-Res Min airflow rate (m3/h/m2) | 4.8077 |  | Feb | 0.49508 | 0.13261 |  | 0.24258 | 0.52427 | 0.54047 | 0.54047 |  | 0.67308 | 0.22436 |  |  |  |  | more than one exposed façade |  |  | one exposed façade |  |  |  | <Source: NEN 2916 Table 6>
| <Source: EN ISO 13789 C.3> |  |  |  | Mar | 0.49508 | 0.13261 |  | 0.19784 | 0.58233 | 0.59701 | 0.59701 |  | 0.72962 | 0.24321 |  | Air leakage level |  |  | Air Leakage Level | [6 empty] | Heat recovery system | η : HR efficiency
[5 empty] | Apr | 0.49508 | 0.13261 |  | 0.15461 | 0.49277 | 0.50248 | 0.50248 |  | 0.63509 | 0.2117 |  | Low (Q4Pa 0.6 m3/h/m2) |  |  | Low | Medium | High | Low | Medium | High |  | No heat recovery | 0
[5 empty] | May | 0.49508 | 0.13261 |  | 0.097036 | 0.34978 | 0.3541 | 0.3541 |  | 0.48671 | 0.16224 |  | Medium (Q4Pa 1.1 m3/h/m2) |  | No shielding | 0.5 | 0.7 | 1.2 | 0.5 | 0.6 | 1 |  | Heat exchange plates or pipes (0.65) | 0.65
| Mechanical Ventilation |  |  |  | Jun | 0.49508 | 0.13261 |  | 0.020353 | 0.49907 | 0.50036 | 0.50036 |  | 0.63297 | 0.21099 |  | High (Q4Pa 2.2 m3/h/m2) |  | Moderate | 0.5 | 0.6 | 0.9 | 0.5 | 0.5 | 0.7 |  | Two-elements-system (0.6) | 0.6
| <Source: EN ISO 13789 C.5> | Supply (m3/h/m2) | 0.49508 |  | Jul | 0.49508 | 0.13261 |  | 0.073963 | 0.4128 | 0.41669 | 0.41669 |  | 0.5493 | 0.1831 |  |  |  | Heavy shielding | 0.5 | 0.5 | 0.6 | 0.5 | 0.5 | 0.5 |  | Loading cold with air-conditioning (0.4) | 0.4
|  | Exhaust (m3/h/m2) | 0.49508 |  | Aug | 0.49508 | 0.13261 |  | 0.035622 | 0.36225 | 0.36389 | 0.36389 |  | 0.4965 | 0.1655 | [11 empty] | Heat-pipes (0.6) | 0.6
|  | Sup-Exh (m3/h/m2) | 0 |  | Sep | 0.49508 | 0.13261 |  | 0.058102 | 0.30977 | 0.31207 | 0.31207 |  | 0.44468 | 0.14823 |  |  |  | EN ISO 13789 Table C.3 | [7 empty] | Slowly rotating or intermittent heat exchangers (0.7) | 0.7
|  | β : mech vent fraction | 0.26786 |  | Oct | 0.49508 | 0.13261 |  | 0.14417 | 0.48544 | 0.49435 | 0.49435 |  | 0.62696 | 0.20899 |  |  |  | Shieding class | Single family air change rate
[5 empty] | Nov | 0.49508 | 0.13261 |  | 0.18884 | 0.5555 | 0.56886 | 0.56886 |  | 0.70147 | 0.23382 |  |  |  |  | more than one exposed façade | [6 empty] | Dropdown menu
|  | η : HR efficiency | 0 | for Heat Recovery | Dec | 0.49508 | 0.13261 |  | 0.25061 | 0.42008 | 0.43349 | 0.43349 |  | 0.5661 | 0.1887 |  |  |  |  | Air Leakage Level | [6 empty] | [Table] Factor for the reduction control of the supply of fresh air
|  |  | 0 | for exhaust air recirculation | Avg | 0.49508 | 0.13261 |  | 0.14344 | 0.45769 | 0.46653 | 0.46653 |  | 0.59914 | 0.19971 |  | Ventilation type |  |  | Low | Medium | High |  |  |  |  | <Source: NEN 2916 6.5.3.7>
|  | fcntrl;vent: recirculation factor | S: 1; E: Cooling |  |  |  |  | Mechanical vent |  | No shielding | 0.5 | 0.8 | 1.5 |  |  |  |  | Exhaust air recirculation % | Factor
[5 empty] | Jan | 0.49508 | 0.13261 |  | 0.3003 | 0.49822 | 0.51728 | 0.51728 |  | 0.64989 | 0.21663 |  | Mechanical vent share w/ Natural |  | Moderate | 0.5 | 0.6 | 1.1 |  |  |  |  | No exhaust air recirculation | 1
[5 empty] | Feb | 0.49508 | 0.13261 |  | 0.28542 | 0.52427 | 0.54333 | 0.54333 |  | 0.67594 | 0.22531 |  | Natural Vent |  | Heavy shielding | 0.5 | 0.5 | 0.7 |  |  |  |  | Exhaust air recirculation 20% | 0.8
[5 empty] | Mar | 0.49508 | 0.13261 |  | 0.23815 | 0.58233 | 0.6 | 0.6 |  | 0.73261 | 0.2442 | [11 empty] | Exhaust air recirculation 40% | 0.6
| Infiltration |  |  |  | Apr | 0.49508 | 0.13261 |  | 0.18772 | 0.49277 | 0.50456 | 0.50456 |  | 0.63717 | 0.21239 | [11 empty] | Exhaust air recirculation 60% | 0.4
| <Source: EN 15242:2007> | Terrain class | 3 |  | May | 0.49508 | 0.13261 |  | 0.14 | 0.34978 | 0.35601 | 0.35601 |  | 0.48862 | 0.16287
|  | vsite/vmetro | 0.8 |  | Jun | 0.49508 | 0.13261 |  | 0.079418 | 0.49907 | 0.50411 | 0.50411 |  | 0.63672 | 0.21224 |  |  |  | EN 15242:2007 Table 3rd Page 44 | [5 empty] | prEN 13379 page 36 for Non-residential for further information | 50
|  | Air leakage Q75Pa(m3/h/m2) based on wall area | 5.41 | Q4pa | Jul | 0.49508 | 0.13261 |  | 0.033466 | 0.4128 | 0.41456 | 0.41456 |  | 0.54717 | 0.18239 |  |  |  | Air leakage level | Q4Pa | Q10Pa | Q50Pa |  |  | Air Tightness | f | l/s/m2 | m3/h/m2 |  | EN 15242:2007 Table A.1 Page38
|  | Q4Pa (m3/h/m2) based on floor area | 1.0992 | convert from 75 to 4 by (4/75)^0.65 | Aug | 0.49508 | 0.13261 |  | 0.070154 | 0.36225 | 0.36548 | 0.36548 |  | 0.49809 | 0.16603 |  |  |  | Multi Family, non-residential | m3/h per floor area |  |  |  |  | Low: class A (f=0.027*Pa^0.65 [liter/s/m2]) | 0.027 | 0.34332 | 1.2359 |  | Terrain Class | vsite/vmetro
|  | Hzone | 4 |  | Sep | 0.49508 | 0.13261 |  | 0.11183 | 0.30977 | 0.31419 | 0.31419 |  | 0.4468 | 0.14893 |  |  |  | Low (Q4Pa 0.6 m3/h/m2) | 0.6 | 1.1 | 2.8 |  |  | Medium: class B (f=0.009*Pa^0.65 [liter/s/m2]) | 0.009 | 0.11444 | 0.41198 |  | Open terrain | 1
|  | dCP for wind impact = | 0.75 |  | Oct | 0.49508 | 0.13261 |  | 0.17843 | 0.48544 | 0.49647 | 0.49647 |  | 0.62908 | 0.20969 |  |  |  | Medium (Q4Pa 1.1 m3/h/m2) | 1.1 | 2.2 | 5.5 |  |  | High: class C (f=0.003*Pa^0.65 [liter/s/m2]) | 0.003 | 0.038146 | 0.13733 |  | Country | 0.9
[5 empty] | Nov | 0.49508 | 0.13261 |  | 0.23097 | 0.5555 | 0.57184 | 0.57184 |  | 0.70445 | 0.23482 |  |  |  | High (Q4Pa 2.2 m3/h/m2) | 2.2 | 3.9 | 11 |  |  | Special: class D (f=0.001*Pa^0.65 [liter/s/m2]) | 0.001 | 0.012715 | 0.045775 |  | Urban / City | 0.8
[5 empty] | Dec | 0.49508 | 0.13261 |  | 0.29354 | 0.42008 | 0.43579 | 0.43579 |  | 0.5684 | 0.18947
[5 empty] | Avg | 0.49508 | 0.13261 |  | 0.17912 | 0.45769 | 0.46863 | 0.46863 |  | 0.60124 | 0.20041
|  | Total Heat Gains (MJ) | N: Total Heat Gain (MJ)
|  | Occupants (MJ) | S: Appliances (MJ); SE: Lighting (MJ); E: Total Internal (MJ); N: QG = Qi + Qs
| Jan | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 327178.714
| Feb | 95835.747 | S: 108036.196; SE: 48170.5818; E: 252042.5248; N: 309468.1482
| Mar | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 356493.8914
| Apr | 102681.1575 | S: 115753.0671; SE: 51611.3377; E: 270045.5623; N: 353535.8811
| May | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 388381.8733
| Jun | 102681.1575 | S: 115753.0671; SE: 51611.3377; E: 270045.5623; N: 379340.611
| Jul | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 392329.9026
| Aug | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 378721.8443
| Sep | 102681.1575 | S: 115753.0671; SE: 51611.3377; E: 270045.5623; N: 356136.1348
| Oct | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 350815.1176
| Nov | 102681.1575 | S: 115753.0671; SE: 51611.3377; E: 270045.5623; N: 314844.8073
| Dec | 106103.8628 | S: 119611.5027; SE: 53331.7156; E: 279047.0811; N: 320682.1703
| Total | 1249287.4165 | S: 1408328.9834; SE: 627937.9416; E: 3285554.3415; N: 4227929.096
HEATING NEED
Building Time Constant for Heating
| Hve | 0 | S: Heat transfer coefficient for ventilation for heating
| aH,0, aC,0 | 1 | S: heating reference constant
| τH,0, τC,0 | 15 | S: heating reference time constant
| τH= Cm /3600/(Htr+Hve) | 53.4163 | S: time constant of the building
| aH=aH,0+τ/τH,0 | 4.5611 | S: dimensionless numerical parameter depending on the time constant
|  | Transmission Loss (MJ) | SE: Ventilation Loss (MJ); E: Total Heat Loss (MJ); SW: Total Heating Need (MJ)
[7 empty] | Heat Gain Ratio |  | Gain utilization factor |  | QNH = QL,H - ηG,H ·QG,H
|  | QT = Σk {HT,k ·( θi - θe,k)}·t | Hve (W/K) | QV = Σk {HV,k ·( θi,z - θs,k)} ·t | QL = QT + QV |  | γH=QG/QL | γ'H | ηG,H |  | subject to QNH >0
| Jan | 293423.9177 | 1482.2509 | 90971.4985 | 384395.4162 |  | 0.85115 | 0.85115 | 0.87943 |  | 96665.4705
| Feb | 242256.2658 | 1541.5733 | 78113.7165 | 320369.9823 |  | 0.96597 | 0.96597 | 0.83408 |  | 62249.1331
| Mar | 197579.9545 | 1671.0659 | 69059.6798 | 266639.6342 |  | 1.337 | 1.337 | 0.68538 |  | 22306.779
| Apr | 132117.6003 | 1454.5612 | 40195.8089 | 172313.4092 |  | 2.0517 | 2.0517 | 0.4778 |  | 3392.9152
| May | 67903.8546 | 1114.7262 | 15832.545 | 83736.3995 |  | 4.6381 | 4.6381 | 0.21545 |  | 60.0179
| Jun | -6319.9998 | 1449.7087 | -1916.3989 | -8236.3988 |  | -46.0566 | 379340.611 | -0.021712 |  | 0
| Jul | -45196.9488 | 1258.0814 | -11893.3986 | -57090.3474 |  | -6.8721 | 392329.9026 | -0.14552 |  | 0
| Aug | -15114.9887 | 1137.1471 | -3595.1134 | -18710.1022 |  | -20.2416 | 378721.8443 | -0.049403 |  | 0
| Sep | 30458.8882 | 1018.4563 | 6488.5034 | 36947.3915 |  | 9.639 | 9.639 | 0.10374 |  | 1.0759
| Oct | 122934.5889 | 1435.9486 | 36923.3493 | 159857.9383 |  | 2.1945 | 2.1945 | 0.44871 |  | 2444.6518
| Nov | 178314.6384 | 1606.5981 | 59921.4558 | 238236.0942 |  | 1.3216 | 1.3216 | 0.69116 |  | 20627.2189
| Dec | 281641.5849 | 1296.5623 | 76379.7555 | 358021.3404 |  | 0.89571 | 0.89571 | 0.86221 |  | 81524.6191
| Total | 1479999.3559 | SE: 456481.4016; E: 1936480.7575; HOR: 289271.8813
COOLING NEED
Building Time Constant for Cooling
| Hve | 0 | S: heat xfer coefficient for ventilattion for cooling
| aH,0, aC,0 | 1 | S: heating reference constant
| τH,0, τC,0 | 15 | S: heating reference time constant
| τC = Cm /3600/H | 53.4163
| aC=a0,C+τC/τ0,C | 4.5611
|  | Transmission Loss (MJ) | S: Ventilation Loss (MJ); E: Total Heat Loss (MJ); SW: Total Cooling Need (MJ) : With Temp Setback YES
[7 empty] | Heat Loss Ratio | Loss Utilization Factor: With Temp Setback YES |  |  | QN,c = QG,C - ηL,C ·QL,C
|  | QT = Σk {HT,k ·( θi - θe,k)}·t | Hve (W/K) | QV = Σk {HV,k ·( θi,z - θs,k)} ·t | QL = QT + QV |  | λC=QL,C/QG,C |  | ηL,C |  | subject to QNC >0
| Jan | 369366.2114 | 1488.4623 | 114996.1012 | 484362.3126 | Jan | 1.4804 | Jan | 0.63421 | Jan | 19993.0627
| Feb | 309149.8836 | 1548.1252 | 100106.7264 | 409256.61 | Feb | 1.3225 | Feb | 0.69083 | Feb | 26741.8515
| Mar | 260906.5296 | 1677.9133 | 91567.7576 | 352474.2872 | Mar | 0.98872 | Mar | 0.8248 | Mar | 65773.9303
| Apr | 176729.3639 | 1459.3207 | 53944.5477 | 230673.9116 | Apr | 0.65248 | Apr | 0.94535 | Apr | 135469.2301
| May | 117642.1168 | 1119.1098 | 27537.444 | 145179.5608 | May | 0.37381 | May | 0.99293 | May | 244228.5487
| Jun | 48663.5252 | 1458.3075 | 14843.6522 | 63507.1774 | Jun | 0.16741 | Jun | 0.99976 | Jun | 315848.6717
| Jul | 13763.9142 | 1253.2048 | 3607.8802 | 17371.7944 | Jul | 0.044279 | Jul | 1 | Jul | 374958.1192
| Aug | 41752.5738 | 1140.7961 | 9962.7536 | 51715.3275 | Aug | 0.13655 | Aug | 0.9999 | Aug | 327011.5971
| Sep | 81293.3921 | 1023.3114 | 17400.0768 | 98693.4689 | Sep | 0.27712 | Sep | 0.99792 | Sep | 257647.6309
| Oct | 169244.1571 | 1440.8007 | 51004.1725 | 220248.3297 | Oct | 0.62782 | Oct | 0.95185 | Oct | 141171.1725
| Nov | 241159.9724 | 1613.4246 | 81384.5563 | 322544.5287 | Nov | 1.0245 | Nov | 0.81013 | Nov | 53541.5386
| Dec | 356971.9551 | 1301.8223 | 97201.709 | 454173.664 | Dec | 1.4163 | Dec | 0.65649 | Dec | 22522.7954
| Total | 2186643.5953 | SE: 663557.3776; E: 2850200.9729; SW: Total; HOR: 1984908.1487
| Fan Energy | T_supply_H (deg C) | S: 27.6; E: [Table] Ventilation fan system; NE: <Source: NEN 2916 7.3.2.3>
|  | T_supply_C (deg C) | S: 17.2; E: Ventilation fan factor; NE: fan factor (W*s/liter)
|  | rho_a_C_a (MJ/m3,K) | S: 0.0012399; E: None; NE: 0
|  | Fan power (Ws/m3) | S: 1.8; E: Only mechanical exhaust; NE: 1.2
|  | Mechanical supply air flow (liter/s) | S: 12246; E: Mechanical supply and exhaust; NE: 2
|  | Mechanical exhaust air flow (liter/s) | S: 12246; E: All other cases; NE: 3
May 2012 Addition
|  | Specifiec fan power [W/(L/s)] | S: 0.51
|  | Fan flow control factor | [10 empty] | OLD Fan Energy Model | bar: S
New Fan Energy Model
|  | Q_H_des (MJ) | deltaT_H=Tsupply_H-Tset_H (deg C) | V_air_H_des (m3) | Q_C_des (MJ) | deltaT_C=Tset_C - Tsupply_C (deg C) | V_air_C_des (m3) | V_air_total (m3) |  | Fan Energy (kWh) | Fan Energy (kWh/m2) |  | E_fan (kWh) | EUI_fan (kWh/m2)
| Jan | 96665.4705 | 9.3306 | 8355495.0204 | 19993.0627 | 7 | 2303510.7439 | 10659005.7643 | Jan | 1510.0258 | 0.21977 |  | 5329.5029 | 0.77565
| Feb | 62249.1331 | 9.1836 | 5466729.1859 | 26741.8515 | 7 | 3081075.8343 | 8547805.0202 | Feb | 1210.939 | 0.17624 |  | 4273.9025 | 0.62202
| Mar | 22306.779 | 8.3454 | 2155759.4261 | 65773.9303 | 7 | 7578176.367 | 9733935.793 | Mar | 1378.9742 | 0.20069 |  | 4866.9679 | 0.70833
| Apr | 3392.9152 | 7 | 390916.4213 | 135469.2301 | 7 | 15608155.2862 | 15999071.7075 | Apr | 2266.5352 | 0.32987 |  | 7999.5359 | 1.1642
| May | 60.0179 | 7 | 6914.9927 | 244228.5487 | 7.2842 | 27040991.9576 | 27047906.9503 | May | 3831.7868 | 0.55768 |  | 13523.9535 | 1.9683
| Jun | 0 | 7 | 0 | 315848.6717 | 7.837 | 32504259.8206 | 32504259.8206 | Jun | 4604.7701 | 0.67017 |  | 16252.1299 | 2.3653
| Jul | 0 | 7 | 0 | 374958.1192 | 8.0044 | 37779912.3225 | 37779912.3225 | Jul | 5352.1542 | 0.77895 |  | 18889.9562 | 2.7492
| Aug | 0 | 7 | 0 | 327011.5971 | 7.841 | 33635867.4296 | 33635867.4296 | Aug | 4765.0812 | 0.69351 |  | 16817.9337 | 2.4477
| Sep | 1.0759 | 7 | 123.9575 | 257647.6309 | 7.5022 | 27698055.1953 | 27698179.1527 | Sep | 3923.9087 | 0.57108 |  | 13849.0896 | 2.0156
| Oct | 2444.6518 | 7.0165 | 281001.1126 | 141171.1725 | 7 | 16265107.4479 | 16546108.5605 | Oct | 2344.032 | 0.34115 |  | 8273.0543 | 1.2041
| Nov | 20627.2189 | 8.4714 | 1963791.9383 | 53541.5386 | 7 | 6168815.2224 | 8502222.8571 | Nov | 1204.4816 | 0.1753 |  | 4251.1114 | 0.6187
| Dec | 81524.6191 | 9.2828 | 7083038.0015 | 22522.7954 | 7 | 2594975.1694 | 9678013.1709 | Dec | 1371.0519 | 0.19954 |  | 4839.0066 | 0.70427
|  |  | W: Total [MJ]; SW: 33763.7409; HOR: 4.9139 |  | 17.3433
District System: added at April 2012
Building connected to DH | bar: S to SE
Efficiency of heating network
|  | Building connected to DH | S: 0; SE: 0: NO; 1: YES (Consumes Natural Gas)
|  | Efficiency of heating network | S: 0.9; SE: Typcial value 0.75 - 0.9: EN 15316-4-5
|  | Efficiency of DH heating system | S: 0.87
|  | Fraction of free heat source to DH | S: 0; SE: Range between 0 and 1 (if none: 0)
District Cooling System
|  | Building connected to DC | S: 0; SE: 0: NO; 1: YES
|  | Efficiency of cooling network | S: 0.9
|  | COP of DC electric chillers | S: 5.5; SE: Refer to the right table
|  | If DC plant has absorption chillers, fraction of cold coming from absorption chillers | S: 0; SE: Range between 0 and 1 (if none: 0)
|  | COP of DC absorption chiller | S: 1; SE: Refer to the right table
|  | Fraction of free heat source to absorption chillers | S: 0; SE: Range between 0 and 1 (if none: 0)
HVAC System
| Heating | Efficiency | S: 0.8
| Cooling | EER | S: 3; SE: by EN15243 Table I.8 (REFERENCE sheet); N: f_dem;heat; NW: 0.1272
|  | PLV | S: 1.05; SE: by EN15243 Table I.12 (REFERENCE sheet); N: f_dem;cold; NW: 0.8728
|  | SEER (ηgen,cool ) | S: 3.15
[6 empty] | For Sensitivity Analysis | ηdist,heat | 0.92593
| Distribution loss | f_waste | 0 | by NEN2916 Table 14 (REFERENCE sheet) | f_waste | 0 | ηdist,cool | 1
|  | a_heat | S: 0.08; SE: by NEN2916 Table 14 (REFERENCE sheet); E: a_heat
|  | a_cool | S: 0; E: a_cool; NE: 0
|  |  | [Table] Ventilation system specification | <source: EN 15243, Table E.1>
system code / heat distribution by / cold distribution by / individual heating control
|  |  | S: System type; SE: Waste Factor f_waste; E: Heating Loss factor a_heat; NE: Cooling loss factor a_cool |  |  |  |  | Waste Factor f_waste | Heating Loss factor a_heat | Cooling loss factor a_cool | System type
|  | 0.08 | S: 1. No airco system / Water or Water&Air / NA / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 1 | 0 | 0.08 | 0 | % 1. No airco system / Water or Water&Air / NA / Yes
|  | 0.25 | S: 2. No airco system / Water or Water&Air / NA / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 2 | 0 | 0.25 | 0 | %2. No airco system / Water or Water&Air / NA / No
|  | 0 | S: 3. No airco system / Air / NA / Yes; SE: 0; E: 0; NE: 0 |  |  |  | 3 | 0 | 0 | 0 | %3. No airco system / Air / NA / Yes
|  | 0.36 | S: 4. No airco system / Air / NA / No; SE: 0; E: 0.36; NE: 0 |  |  |  | 4 | 0 | 0.36 | 0 | %4. No airco system / Air / NA / No
|  | 0.12 | S: 5. Single duct system / Water or Water&Air / Water / Yes; SE: 0.03; E: 0.08; NE: 0.01 |  |  |  | 5 | 0.03 | 0.08 | 0.01 | %5. Single duct system / Water or Water&Air / Water / Yes
|  | 0.08 | S: 6 .Single duct system / Water or Water&Air / Air / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 6 | 0 | 0.08 | 0 | %6 .Single duct system / Water or Water&Air / Air / Yes
|  | 0.25 | S: 7. Single duct system / Water or Water&Air / Air / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 7 | 0 | 0.25 | 0 | %7. Single duct system / Water or Water&Air / Air / No
|  | 0.04 | S: 8. Single duct system / Air / Air / Yes; SE: 0.04; E: 0; NE: 0 |  |  |  | 8 | 0.04 | 0 | 0 | %8. Single duct system / Air / Air / Yes
|  | 0.36 | S: 9. Single duct system / Air / Air / No; SE: 0; E: 0.36; NE: 0 |  |  |  | 9 | 0 | 0.36 | 0 | %9. Single duct system / Air / Air / No
|  | 0.12 | S: 10. Dual duct system / Water or Water&Air / Water / Yes; SE: 0.03; E: 0.08; NE: 0.01 |  |  |  | 10 | 0.03 | 0.08 | 0.01 | %10. Dual duct system / Water or Water&Air / Water / Yes
|  | 0.08 | S: 11. Dual duct system / Water or Water&Air / Air / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 11 | 0 | 0.08 | 0 | %11. Dual duct system / Water or Water&Air / Air / Yes
|  | 0.25 | S: 12. Dual duct system / Water or Water&Air / Air / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 12 | 0 | 0.25 | 0 | %12. Dual duct system / Water or Water&Air / Air / No
|  | 0.09 | S: 13. Dual duct system / Air / Water / Yes; SE: 0.08; E: 0; NE: 0.01 |  |  |  | 13 | 0.08 | 0 | 0.01 | %13. Dual duct system / Air / Water / Yes
|  | 0.12 | S: 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes; SE: 0.03; E: 0.08; NE: 0.01 |  |  |  | 14 | 0.03 | 0.08 | 0.01 | %14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes
|  | 0.08 | S: 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 15 | 0 | 0.08 | 0 | %15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes
|  | 0.25 | S: 16. Single duct , Terminal reheat / Water or Water&Air / Air / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 16 | 0 | 0.25 | 0 | %16. Single duct , Terminal reheat / Water or Water&Air / Air / No
|  | 0.12 | S: 17. Constant volume / Water or Water&Air / Water / Yes; SE: 0.03; E: 0.08; NE: 0.01 |  |  |  | 17 | 0.03 | 0.08 | 0.01 | %17. Constant volume / Water or Water&Air / Water / Yes
|  | 0.08 | S: 18. Constant volume / Water or Water&Air / Air / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 18 | 0 | 0.08 | 0 | %18. Constant volume / Water or Water&Air / Air / Yes
|  | 0.25 | S: 19. Constant volume / Water or Water&Air / Air / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 19 | 0 | 0.25 | 0 | %19. Constant volume / Water or Water&Air / Air / No
|  | 0.04 | S: 20. Constant volume / Air / Air / Yes; SE: 0.04; E: 0; NE: 0 |  |  |  | 20 | 0.04 | 0 | 0 | %20. Constant volume / Air / Air / Yes
|  | 0.36 | S: 21. Constant volume / Air / Air / No; SE: 0; E: 0.36; NE: 0 |  |  |  | 21 | 0 | 0.36 | 0 | %21. Constant volume / Air / Air / No
|  | 0.12 | S: 22. VAV / Water or Water&Air / Water / Yes; SE: 0.03; E: 0.08; NE: 0.01 |  |  |  | 22 | 0.03 | 0.08 | 0.01 | %22. VAV / Water or Water&Air / Water / Yes
|  | 0.08 | S: 23. VAV / Water or Water&Air / Air / Yes; SE: 0; E: 0.08; NE: 0 |  |  |  | 23 | 0 | 0.08 | 0 | %23. VAV / Water or Water&Air / Air / Yes
|  | 0.25 | S: 24. Variable air volume / Water or Water&Air / Air / No; SE: 0; E: 0.25; NE: 0 |  |  |  | 24 | 0 | 0.25 | 0 | %24. Variable air volume / Water or Water&Air / Air / No
|  | 0.13 | S: 25. Fan coil unit system; SE: 0.04; E: 0.08; NE: 0.01 |  |  |  | 25 | 0.04 | 0.08 | 0.01 | %25. Fan coil unit system
|  | 0 | [13 empty] | 26
|  | 0 | [13 empty] | 27
|  | 0.09 | S: 28. Induction system, non change over; SE: 0.08; E: 0; NE: 0.01 |  |  |  | 28 | 0.08 | 0 | 0.01 | %28. Induction system, non change over
|  | 0.13 | S: 29. Induction system, change over; SE: 0.04; E: 0.08; NE: 0.01 |  |  |  | 29 | 0.04 | 0.08 | 0.01 | %29. Induction system, change over
|  | 0 | [13 empty] | 30
|  | 0 | [13 empty] | 31
|  | 0.13 | S: 32. Radiant cooling panels (chilled ceilings & passive chilled beams); SE: 0.04; E: 0.08; NE: 0.01 |  |  |  | 32 | 0.04 | 0.08 | 0.01 | %32. Radiant cooling panels (chilled ceilings & passive chilled beams)
|  | 0 | [13 empty] | 33
|  | 0.13 | S: 34. Embedded cooling system floors, walls or ceilings; SE: 0.04; E: 0.08; NE: 0.01 |  |  |  | 34 | 0.04 | 0.08 | 0.01 | %34. Embedded cooling system floors, walls or ceilings
|  | 0 | S: 35. Room units including single duct units; SE: 0; E: 0; NE: 0 |  |  |  | 35 | 0 | 0 | 0 | %35. Room units including single duct units
|  | 0 | S: 36. Direct expansion single split system; SE: 0; E: 0; NE: 0 |  |  |  | 36 | 0 | 0 | 0 | %36. Direct expansion single split system
|  |  |  | Qheat,an=Σi ((Qheat_nd,i + Qloss,heat,i) / ηgen,heat) |  |  | Qcool,an=Σi ((Qcool_nd,i + Qloss,cool,i) / ηgen,cool)
|  | Q_loss_heat (MJ) | SE: E_heat (MJ); NE: Q_loss_cool (MJ); N: Q_cool (MJ)
| Jan | 7733.2376 | SE: 130498.3852; NE: 0; N: 6347.004
| Feb | 4979.9306 | SE: 84036.3296; NE: 0; N: 8489.4767
| Mar | 1784.5423 | SE: 30114.1516; NE: 0; N: 20880.6128
| Apr | 271.4332 | SE: 4580.4355; NE: 0; N: 43006.1048
| May | 4.8014 | SE: 81.0242; NE: 0; N: 77532.8726
| Jun | 0 | SE: 0; NE: 0; N: 100269.4196
| Jul | 0 | SE: 0; NE: 0; N: 119034.3236
| Aug | 0 | SE: 0; NE: 0; N: 103813.2054
| Sep | 0.08607 | SE: 1.4524; NE: 0; N: 81792.8987
| Oct | 195.5721 | SE: 3300.2799; NE: 0; N: 44816.2453
| Nov | 1650.1775 | SE: 27846.7455; NE: 0; N: 16997.3138
| Dec | 6521.9695 | SE: 110058.2358; NE: 0; N: 7150.0938
| Total [MJ] | 23141.7505 | SE: 390517.0397; NE: 0; N: 630129.571
DC |  |  | S: Elec; SE: Natural Gas; NE: DH; NW: Natural Gas
|  | Q_cool_nd for DC (MJ) | S: E_cool_dc_elec; SE: E_cool_dc_absorp; N: Q_heat_nd for DH (MJ); NW: E_heat_dh(MJ)
| Jan | 0 | S: 0; SE: 0; NE: Jan; N: 0; NW: 0
| Feb | 0 | S: 0; SE: 0; NE: Feb; N: 0; NW: 0
| Mar | 0 | S: 0; SE: 0; NE: Mar; N: 0; NW: 0
| Apr | 0 | S: 0; SE: 0; NE: Apr; N: 0; NW: 0
| May | 0 | S: 0; SE: 0; NE: May; N: 0; NW: 0
| Jun | 0 | S: 0; SE: 0; NE: Jun; N: 0; NW: 0
| Jul | 0 | S: 0; SE: 0; NE: Jul; N: 0; NW: 0
| Aug | 0 | S: 0; SE: 0; NE: Aug; N: 0; NW: 0
| Sep | 0 | S: 0; SE: 0; NE: Sep; N: 0; NW: 0
| Oct | 0 | S: 0; SE: 0; NE: Oct; N: 0; NW: 0
| Nov | 0 | S: 0; SE: 0; NE: Nov; N: 0; NW: 0
| Dec | 0 | S: 0; SE: 0; NE: Dec; N: 0; NW: 0
| Total [MJ] | 0 | S: 0; SE: 0; NE: Total [MJ]; N: 0; NW: 0
|  | TOTAL ELECTRICITY USE FOR HEATING ANDCOOLING | E: TOTAL NATURAL GAS USE FOR HEATING AND COOLING
|  | E_heat [MJ] | S: E_cool [MJ]; E: E_heat [MJ]; NE: E_cool [MJ]
| Jan | 0 | S: 6347.004; E: 130498.3852; NE: 0
| Feb | 0 | S: 8489.4767; E: 84036.3296; NE: 0
| Mar | 0 | S: 20880.6128; E: 30114.1516; NE: 0
| Apr | 0 | S: 43006.1048; E: 4580.4355; NE: 0
| May | 0 | S: 77532.8726; E: 81.0242; NE: 0
| Jun | 0 | S: 100269.4196; E: 0; NE: 0
| Jul | 0 | S: 119034.3236; E: 0; NE: 0
| Aug | 0 | S: 103813.2054; E: 0; NE: 0
| Sep | 0 | S: 81792.8987; E: 1.4524; NE: 0
| Oct | 0 | S: 44816.2453; E: 3300.2799; NE: 0
| Nov | 0 | S: 16997.3138; E: 27846.7455; NE: 0
| Dec | 0 | S: 7150.0938; E: 110058.2358; NE: 0
| Total [MJ] | 0 | S: 630129.571; E: 390517.0397; NE: 0
Air Handling Unit: added at May 2012 (EPA NR 2007 6.9.3.5)
|  | Q_ahu,h | S: =f_h * Q_dem_ahu_h
|  | Q_dem_ahu_h | S: = H_h_ahu * ((T_h_supp - deltaT_fans)-T_mix) * f_vent * t; E: f_recir; NW: Local heating unit: 0: NO; 1: YES
|  | T_mix | S: = f_mix * T_return + (1 - f_mix) * T_e; E: 1; NW: 1
|  | T_return | S: = T_i; E: eta_hr; NW: YES: T_h_supp = T_h_supp_set
[5 empty] | 1 |  |  | NO: T_h_supp=T_mix +deltaT_fans
| Heating |  | T_return (T_i) | T_e | f_mix | T_mix | deltaT_fans | T_h_supp | f_vent | H_h_ahu | t | Q_dem_ahu_h (MJ) | Q_nd_h (MJ) | Q'_nd_h (MJ) | f_h | Q_ahu,h
|  | Jan | 18.2694 | -4.645 | 0 | -4.645 | 0.4 | 27.6 | 0.26786 | 2819.144 | 2.6784 | 64407.5148 | 96665.4705 | 161072.9853 | 0.83447 | 53746.3575
|  | Feb | 18.4164 | -2.5292 | 0 | -2.5292 | 0.4 | 27.6 | 0.26786 | 1844.4744 | 2.4192 | 35532.8776 | 62249.1331 | 97782.0107 | 0.71091 | 25260.7242
|  | Mar | 19.2546 | 3.825 | 0 | 3.825 | 0.4 | 27.6 | 0.26786 | 727.3532 | 2.6784 | 12197.6357 | 22306.779 | 34504.4147 | 0.27808 | 3391.9599
|  | Apr | 20.6 | 9.9386 | 0 | 9.9386 | 0.4 | 27.6 | 0.26786 | 131.8952 | 2.592 | 1580.6764 | 3392.9152 | 4973.5915 | 0.030047 | 47.4938
|  | May | 20.6 | 15.2972 | 0 | 15.2972 | 0.4 | 27.6 | 0.26786 | 2.3331 | 2.6784 | 19.9235 | 60.0179 | 79.9414 | 0.00031455 | 0.0062669
|  | Jun | 20.6 | 21.11 | 0 | 21.11 | 0.4 | 27.6 | 0.26786 | 0 | 2.592 | 0 | 0 | 0 | 0 | 0
|  | Jul | 20.6 | 24.1296 | 0 | 24.1296 | 0.4 | 27.6 | 0.26786 | 0 | 2.6784 | 0 | 0 | 0 | 0 | 0
|  | Aug | 20.6 | 21.7804 | 0 | 21.7804 | 0.4 | 27.6 | 0.26786 | 0 | 2.6784 | 0 | 0 | 0 | 0 | 0
|  | Sep | 20.6 | 18.1421 | 0 | 18.1421 | 0.4 | 27.6 | 0.26786 | 0.041823 | 2.592 | 0.26302 | 1.0759 | 1.3389 | 5.3783e-06 | 1.4146e-06
|  | Oct | 20.5835 | 10.9832 | 0 | 10.9832 | 0.4 | 27.6 | 0.26786 | 94.8098 | 2.6784 | 1103.0545 | 2444.6518 | 3547.7063 | 0.021165 | 23.3463
|  | Nov | 19.1286 | 4.7393 | 0 | 4.7393 | 0.4 | 27.6 | 0.26786 | 662.5834 | 2.592 | 10332.4178 | 20627.2189 | 30959.6367 | 0.30374 | 3138.3229
|  | Dec | 18.3172 | -3.677 | 0 | -3.677 | 0.4 | 27.6 | 0.26786 | 2389.817 | 2.6784 | 52939.4076 | 81524.6191 | 134464.0267 | 0.79167 | 41910.3662
|  | Q_ahu_c | S: =f_c * Q_dem_ahu_c
|  | Q_dem_ahu_c | S: = H_c_ahu * ((T_c_supp - deltaT_fans)-T_mix) * f_vent * t; NW: Local cooling unit: 0: NO; 1: YES
|  | T_mix | S: = f_mix * T_return + (1 - f_mix) * T_e; NW: 1
|  | T_return | S: = T_i; NW: YES: T_c_supp = T_c_supp_set
NO: T_c_supp=T_mix +deltaT_fans
TBD
|  |  | T_return (T_i) | T_e | f_mix | T_mix | deltaT_fans | T_c_supp | f_vent | H_c_ahu | t | Q_dem_ahu_c (MJ) | Q_nd_c (MJ) | Q'_nd_c (MJ) | f_c | Q_ahu,h | X_e (g/kg dry air) | X_supp (g/kg dry air)
| Cooling | Jan | 24.2 | -4.645 | 0 | -4.645 | 0.4 | 17.2 | 0.26786 | 777.2045 | 2.6784 | 11957.4641 | 19993.0627 | 31950.5268 | 0.16553 | 1979.2784 | 1 | 1
|  | Feb | 24.2 | -2.5292 | 0 | -2.5292 | 0.4 | 17.2 | 0.26786 | 1039.555 | 2.4192 | 13020.7381 | 26741.8515 | 39762.5896 | 0.28909 | 3764.1482 | 1 | 1
|  | Mar | 24.2 | 3.825 | 0 | 3.825 | 0.4 | 17.2 | 0.26786 | 2556.8767 | 2.6784 | 23801.0338 | 65773.9303 | 89574.9641 | 0.72192 | 17182.3616 | 1 | 1
|  | Apr | 24.2 | 9.9386 | 0 | 9.9386 | 0.4 | 17.2 | 0.26786 | 5266.1916 | 2.592 | 25086.8954 | 135469.2301 | 160556.1255 | 0.96995 | 24333.1216 | 1 | 1
|  | May | 24.4842 | 15.2972 | 0 | 15.2972 | 0.4 | 17.2 | 0.26786 | 9123.6307 | 2.6784 | 9836.8053 | 244228.5487 | 254065.354 | 0.99969 | 9833.7112 | 1 | 1
|  | Jun | 25.037 | 21.11 | 0 | 21.11 | 0.4 | 17.2 | 0.26786 | 10966.9373 | 2.592 | -32817.1497 | 315848.6717 | 283031.5219 | 1 | -32817.1497 | 1 | 1
|  | Jul | 25.2044 | 24.1296 | 0 | 24.1296 | 0.4 | 17.2 | 0.26786 | 12746.9424 | 2.6784 | -67029.0683 | 374958.1192 | 307929.0509 | 1 | -67029.0683 | 1 | 1
|  | Aug | 25.041 | 21.7804 | 0 | 21.7804 | 0.4 | 17.2 | 0.26786 | 11348.7417 | 2.6784 | -40549.7836 | 327011.5971 | 286461.8136 | 1 | -40549.7836 | 1 | 1
|  | Sep | 24.7022 | 18.1421 | 0 | 18.1421 | 0.4 | 17.2 | 0.26786 | 9345.3238 | 2.592 | -8707.8726 | 257647.6309 | 248939.7583 | 0.99999 | -8707.8258 | 1 | 1
|  | Oct | 24.2 | 10.9832 | 0 | 10.9832 | 0.4 | 17.2 | 0.26786 | 5487.8473 | 2.6784 | 22901.551 | 141171.1725 | 164072.7235 | 0.97883 | 22416.8369 | 1 | 1
|  | Nov | 24.2 | 4.7393 | 0 | 4.7393 | 0.4 | 17.2 | 0.26786 | 2081.3583 | 2.592 | 17428.3946 | 53541.5386 | 70969.9332 | 0.69626 | 12134.7711 | 1 | 1
|  | Dec | 24.2 | -3.677 | 0 | -3.677 | 0.4 | 17.2 | 0.26786 | 875.5446 | 2.6784 | 12862.4672 | 22522.7954 | 35385.2626 | 0.20833 | 2679.6802 | 1 | 1
Pump Energy
Dropdown menu
|  |  | #REF! |  |  | [Table] Weighting factor for flow control in cold water circuits |  |  | Total [MJ] | #REF!
|  | fcntrl;cool: Pump control weighting factor for cooling | S: #REF!; NE: <Source: NEN 2916 9.4.3>; W: Month; SW: Pump Energy
|  |  | #REF! |  | Cooling | Control | Factor |  | Jan | #REF!
|  | fcntrl;heat: Pump control weighting factor for heating | S: #REF!; NE: Weighting; N: Factor; W: Feb; SW: #REF!
[6 empty] | No pump for cooling | 0 |  | Mar | #REF!
|  | Multiplication factor | S: 8; NE: Automatic control more than 50%; N: 0.5; W: Apr; SW: #REF!
[6 empty] | All other cases | 1 |  | May | #REF!
|  | Pump energy usage hourly (W/m2) | S: #REF!; W: Jun; SW: #REF!
[6 empty] | Dropdown menu |  |  | Jul | #REF!
[6 empty] | [Table] Weighting factor for flow control in warm water circuits |  |  | Aug | #REF!
[6 empty] | <Source: NEN 2916 9.4.3> |  |  | Sep | #REF!
[5 empty] | Heating | Control | Factor |  | Oct | #REF!
[6 empty] | No pump for heating | 0 |  | Nov | #REF!
[6 empty] | Automatic control more than 50% | 0.5 |  | Dec | #REF!
[6 empty] | All other cases | 1
May 2012 Addition (EPA NR 2007 6.9.7.1, 6.9.7.2), Ignore above
|  | #REF! | S: 1; E: Cooling pumps control factor; NE: 1
|  |  | Heating pump operational factor | Heating Pumps Energy (MJ) |  | Cooling pump operational factor | Cooling Pumps Energy (MJ) |  | Total Pump Operational factor | Total Pump Energy (MJ)
|  | Jan | 0.82862 | 15789.2192 |  | 0.17138 | 1033.4819 |  | 0.051297 | 5639.3831 | 16822.7011 | 413332.7307
|  | Feb | 0.6995 | 13328.8626 |  | 0.3005 | 1812.1141 |  | 0.039131 | 4301.9078 | 15140.9767 | 322798.8973
|  | Mar | 0.25325 | 4825.7171 |  | 0.74675 | 4503.1152 |  | 0.038731 | 4257.9043 | 9328.8323 | 209100.9782
|  | Apr | 0.024434 | 465.5807 |  | 0.97557 | 5882.9731 |  | 0.06106 | 6712.7266 | 6348.5538 | 98452.6543
|  | May | 0.00024568 | 4.6815 |  | 0.99975 | 6028.8345 |  | 0.10742 | 11809.1389 | 6033.5159 | 82075.3694
|  | Jun | 0 | 0 |  | 1 | 6030.316 |  | 0.13888 | 15268.4216 | 6030.316 | 139335.0958
|  | Jul | 0 | 0 |  | 1 | 6030.316 |  | 0.16488 | 18125.8279 | 6030.316 | 190301.7399
|  | Aug | 0 | 0 |  | 1 | 6030.316 |  | 0.14379 | 15808.0479 | 6030.316 | 149755.6606
|  | Sep | 4.1757e-06 | 0.079568 |  | 1 | 6030.2908 |  | 0.11329 | 12454.9806 | 6030.3704 | 97101.7532
|  | Oct | 0.017022 | 324.3549 |  | 0.98298 | 5927.667 |  | 0.063151 | 6942.5239 | 6252.0219 | 89643.0512
|  | Nov | 0.27811 | 5299.385 |  | 0.72189 | 4353.213 |  | 0.032613 | 3585.3874 | 9652.598 | 187588.3165
|  | Dec | 0.78353 | 14930.1194 |  | 0.21647 | 1305.3623 |  | 0.045752 | 5029.7498 | 16235.4818 | 390337.753
|  | Total [MJ] | 2.8847 | 54968 | 54968 | 9.1153 | 54968 | 54968 | 1 | 109936 | 109936
DHW and Solar Water Heating
|  | DHW energy usage calculation | NE: Dropdown menu; W: Dropdown menu
|  | Qdhw= ((Qdem;DWH/ηsys;DHW) - Qses;DHW)/ηgen;DHW | NE: [Table]DHW distribution system efficiency; W: DHW generation system efficiency
|  | <Source: NEN 2916 12.2> | NE: <Source: NEN 2916 12.4>; W: <Source: NEN 2916 12.6.2 Table 34>
[6 empty] | All Taps Within 3m from Heat Generation | 1 |  | Electric | 0.75
|  | Water setpoint temperature [C] | S: 60; NE: Taps More Than 3m from Heat Generation; N: 0.8; W: High-efficiency elec boiler; SW: 0.9
|  | Water initial temperature [C] | S: 20; NE: Circulation system or Unknown; N: 0.6; W: Gas Boiler, HR-Boiler; SW: 0.748
|  | Annual water consumption [m3/yr] | S: 268; W: Co-Generation; SW: 0.9
|  | Qdem,yr (MJ/yr) | S: 44809.6; W: District Heating; SW: 0.9
[9 empty] | Heat Pump | 1.4
[9 empty] | Steam | 0.6075
For Parameter Screening
|  | ηsys;DHW | 0.8 | 0.8 |  | Month | Qdem (kWh) | Esol_hours (kWh/m2) | Esol (kWh/m2) | Qses (kwh) | DHW system (kWh) | Edel_dhw (kWh)
|  | ηgen;DHW | 0.8 |  |  | Jan | 1054.1919 | 54.7566 | 3500.1848 | 0 | 1317.7398 | 1647.1748
[6 empty] | Feb | 952.1733 | 69.814 | 4462.6933 | 0 | 1190.2166 | 1487.7708
[6 empty] | Mar | 1054.1919 | 106.645 | 6817.0271 | 0 | 1317.7398 | 1647.1748
|  | Solar water heating contribution |  |  |  | Apr | 1020.1857 | 131.824 | 8426.5346 | 0 | 1275.2321 | 1594.0401
|  | Qses= 0.5* Ases,DHW* Esol_hours*Ftilt [kWh] |  |  |  | May | 1054.1919 | 185.252 | 11841.7919 | 0 | 1317.7398 | 1647.1748
|  | <Source: NEN 12.5 and Huafen equation> |  |  |  | Jun | 1020.1857 | 188.805 | 12068.909 | 0 | 1275.2321 | 1594.0401
[6 empty] | Jul | 1054.1919 | 191.48 | 12239.902 | 0 | 1317.7398 | 1647.1748
|  | Solar Collector Surface (m2) | 0 |  |  | Aug | 1054.1919 | 160.004 | 10227.8738 | 0 | 1317.7398 | 1647.1748
|  |  | 12 |  |  | Sep | 1020.1857 | 125.779 | 8040.1224 | 0 | 1275.2321 | 1594.0401
|  | Ftilt | 63.9226 |  |  | Oct | 1054.1919 | 91.177 | 5828.2721 | 0 | 1317.7398 | 1647.1748
|  | Solar Collector Efficiency | 0.5 | <Source: NEN 2916 12.5> |  | Nov | 1020.1857 | 54.559 | 3487.5539 | 0 | 1275.2321 | 1594.0401
[6 empty] | Dec | 1054.1919 | 46.5614 | 2976.3275 | 0 | 1317.7398 | 1647.1748
[6 empty] | Total | 12412.2592 | 1406.657 | 89917.1923 | 0 | 15515.324 | 19394.155
Appliances
[6 empty] | Month | Electricity [kWh/m2] | NG [kWh/m2]
|  | Electricity powered appliances [W/m2] | S: NG powered appliances [W/m2]; SE: Fraction; NE: Jan; N: 4.0265; NW: 0.8091
| Occupied | 9.9 | S: 4.06; SE: 26.79%; NE: Feb; N: 3.6368; NW: 0.7308
| Unoccupied | 3.77 | S: 0; SE: 73.21%; NE: Mar; N: 4.0265; NW: 0.8091
| All averaged | 5.412 | S: 1.0875; NE: Apr; N: 3.8966; NW: 0.783
[6 empty] | May | 4.0265 | 0.8091
[6 empty] | Jun | 3.8966 | 0.783
[6 empty] | Jul | 4.0265 | 0.8091
[6 empty] | Aug | 4.0265 | 0.8091
[6 empty] | Sep | 3.8966 | 0.783
[6 empty] | Oct | 4.0265 | 0.8091
[6 empty] | Nov | 3.8966 | 0.783
[6 empty] | Dec | 4.0265 | 0.8091
[6 empty] | Total | 47.4088 | 9.5265
Energy Generation
[13 empty] | 0 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 | 45 | 60 | 60 | 60 | 60 | 60 | 90 | 90 | 90 | 90 | 90
Electricity | [13 empty] | South | South-East | East | West | South-West | South | South-East | East | West | South-West | South | South-East | East | West | South-West | South | South-East | East | West | South-West |  |  |  | Avg Esol (W/m2) |  |  | Month | Esol_hours (kWh/m2) | Edel_pv (kwh) | Edel_pv (MJ)
| Photovoltaic System | PV module Surface Area (m2) | S: 0 | 68.7887 | 112.8956 | 71.7009 | 84.0855 | 55.7635 | 79.6492 | 127.7814 | 81.2821 | 82.1977 | 55.2651 | 87.7921 | 134.0206 | 87.0027 | 73.4542 | 55.4708 | 96.1174 | 114.6992 | 81.3552 | 25.8322 | 55.202 | 98.2782 |  |  |  | 68.7887 |  |  | Jan | 51.1788 | 0 | 0
[13 empty] | 93.1607 | 143.4939 | 79.0956 | 107.8192 | 85.3053 | 105.0974 | 158.3413 | 90.2892 | 105.8147 | 88.3912 | 113.671 | 161.9167 | 98.705 | 95.4145 | 87.2214 | 120.7804 | 130.8826 | 96.8192 | 34.6888 | 71.6222 | 114.7622 |  |  |  | 93.1607 |  |  | Feb | 62.604 | 0 | 0
|  | Kpk (KW/m2) | S: 0 | 125.1116 | 176.0594 | 97.1732 | 135.3224 | 106.6574 | 126.5799 | 186.525 | 105.0277 | 135.2626 | 109.6139 | 133.1982 | 182.5233 | 113.6992 | 124.7167 | 106.9895 | 134.8065 | 130.6444 | 111.5446 | 51.39 | 85.9274 | 117.9532 |  |  |  | 125.1116 |  |  | Mar | 93.083 | 0 | 0
[13 empty] | 169.3958 | 211.6649 | 108.4646 | 150.0708 | 131.0079 | 147.2507 | 213.0351 | 109.5715 | 153.9881 | 136.1234 | 151.4974 | 196.9193 | 116.4101 | 146.5954 | 136.0158 | 148.9121 | 118.91 | 118.2833 | 80.6825 | 116.1468 | 126.8178 |  |  |  | 169.3958 |  |  | Apr | 121.965 | 0 | 0
|  | Fperf | S: 0 | 225.5228 | 256.0864 | 138.5135 | 166.9442 | 194.1601 | 191.6665 | 250.2974 | 134.9861 | 171.7999 | 199.2652 | 194.3341 | 223.3009 | 131.2122 | 164.6446 | 195.6136 | 186.683 | 119.6109 | 122.6935 | 119.3306 | 157.2135 | 150.4544 |  |  |  | 225.5228 |  |  | May | 167.789 | 0 | 0
[13 empty] | 249.375 | 266.9117 | 148.2385 | 180.0405 | 183.4378 | 161.6329 | 257.8768 | 143.0652 | 187.1282 | 189.5806 | 165.7667 | 226.7444 | 134.1764 | 181.4357 | 188.9822 | 165.4948 | 115.2961 | 130.4936 | 132.6923 | 165.1745 | 148.505 |  |  |  | 249.375 |  |  | Jun | 179.55 | 0 | 0
|  | Ppk (KW) | S: 0 | 258.1747 | 289.4057 | 148.2151 | 189.7922 | 200.3488 | 187.655 | 279.9033 | 144.3842 | 197.6912 | 205.2651 | 189.893 | 246.8025 | 140.0819 | 192.0089 | 201.7196 | 182.8524 | 126.8283 | 143.1472 | 127.169 | 162.4508 | 153.6571 |  |  |  | 258.1747 |  |  | Jul | 192.082 | 0 | 0
[13 empty] | 223.8898 | 266.5429 | 128.6559 | 174.8463 | 178.2427 | 179.5597 | 264.3415 | 128.2886 | 179.6582 | 183.8016 | 185.5273 | 240.5806 | 134.3803 | 171.6644 | 181.1272 | 183.6255 | 139.097 | 138.145 | 105.0263 | 149.8421 | 157.4486 |  |  |  | 223.8898 |  |  | Aug | 166.574 | 0 | 0
[13 empty] | 185.4375 | 241.8779 | 110.6299 | 156.4102 | 145.0591 | 158.1229 | 249.3672 | 117.7839 | 158.7987 | 151.9114 | 167.0214 | 237.7582 | 130.6122 | 149.3813 | 153.1545 | 172.2363 | 160.225 | 135.5426 | 77.7035 | 132.1623 | 163.427 |  |  |  | 185.4375 |  |  | Sep | 133.515 | 0 | 0
[13 empty] | 117.9919 | 171.5023 | 94.0345 | 123.6167 | 108.4587 | 142.5193 | 185.5568 | 104.91 | 123.2698 | 110.8346 | 150.808 | 186.0942 | 114.2271 | 113.2778 | 108.5356 | 153.43 | 143.1756 | 112.0658 | 46.4651 | 87.176 | 128.1488 |  |  |  | 117.9919 |  |  | Oct | 87.786 | 0 | 0
[13 empty] | 97.5361 | 159.9842 | 86.2662 | 108.2742 | 77.6876 | 114.324 | 180.2709 | 102.1456 | 106.1093 | 79.5311 | 124.3145 | 188.3199 | 113.6762 | 95.5797 | 79.1006 | 135.2338 | 161.5788 | 114.5156 | 30.5023 | 72.955 | 135.6304 |  |  |  | 97.5361 |  |  | Nov | 70.226 | 0 | 0
[13 empty] | 68.3987 | 120.3616 | 71.5695 | 80.0117 | 63.9226 | 103.6558 | 138.1749 | 84.1153 | 78.0408 | 64.8156 | 113.9689 | 146.8349 | 92.1646 | 69.7728 | 63.6251 | 119.583 | 130.8112 | 89.8624 | 21.5771 | 54.7786 | 109.2564 |  |  |  | 68.3987 |  |  | Dec | 50.8886 | 0 | 0
|  |  | Total: sum | 1882.7834 | 2416.7866 | 1282.5575 | 1657.2339 | 1530.0514 | 1697.7133 | 2491.4716 | 1345.8495 | 1679.7592 | 1574.3988 | 1777.7926 | 2371.8155 | 1406.3478 | 1577.946 | 1557.5559 | 1799.7553 | 1591.759 | 1394.4681 | 853.0596 | 1310.6512 | 1604.3392 |  |  |  | 1882.7834 |  |  | Total | 1377.2414 | 0 | 0
Weather Data |  |  | Total: factor | 1 | 1.2836 | 0.6812 | 0.8802 | 0.81265 | 0.9017 | 1.3233 | 0.71482 | 0.89217 | 0.83621 | 0.94424 | 1.2597 | 0.74695 | 0.83809 | 0.82726 | 0.9559 | 0.84543 | 0.74064 | 0.45308 | 0.69612 | 0.85211
[14 empty] | Temps | [23 empty] | Global Hor. Radiation (W/m2) | [29 empty] | Radiation
Old Reference Value Based on Regression
| COEFFICIENTS | nd | S: del; SE: pri
| Intercept | 0.56103 | S: 0.74648; SE: 0.67364
| Occ_hour_norm | 0.37977 | S: 0.25617; SE: 0.31814
| Occ_hour_norm/Occ_density_bar^2 | 0.046293 | S: 0.0059765; SE: 0.0082782
| BASELINE | Base | S: Normalized
| Occ Hour (hr/wk) | 75 | S: 0.6
| Occ Density (m2/p) | 19.32 | S: 0.32298
| EUI: Total Thermal Need | 68.9002
| EUI: Total Delivered | 139.1411
| EUI: Total Primary | 448.945
New Reference Value
| PPD Reference | 10.76
Standardized Operation
| SqFt (ft2) | 73958.8285
| PCs (W/m2) | 2.69 | S: 1/4 of Appliances
| Hours/week | 45
| Occupant density (m2/p) | 6.24
| Metabolic rate (W/p) | 80
| PC Power (W/PC) | 125 | S: CIBSE Guide A 6.4.4
Translate to EnergyStar
| Operating Characteristic | Formula to Compute variable | S: Building Variable Value; SE: Reference Centering Value; E: Building Centered Variable (Variable Value - Center Value); NE: Coefficient; N: Coefficient * Centered Variable
| Constant | NA | S: NA; SE: NA; E: NA; NE: 186.6; N: 186.6
| CLnSqFt | LN(Square Foot) | S: 11.2113; SE: 9.535; E: 1.6763; NE: 34.17; N: 57.2779
| CPCDen | #Computers/ft2*1000 | S: 1.9993; SE: 2.231; E: -0.23173; NE: 17.28; N: -4.0042
| CLNWkHrs | LN(Weekly Operating Hours) | S: 3.8067; SE: 3.972; E: -0.16534; NE: 55.96; N: -9.2523
| CLNWkrDen | LN(#Workers/ft2*1000) | S: 2.7006; SE: 0.5616; E: 2.139; NE: 10.34; N: 22.117
| CHDDxPH | (HDD*Percent Heated) | S: 3106; SE: 4411; E: -1305; NE: 0.0077; N: -10.0485
| CCDDxPC | (CDD*Percent Cooled) | S: 691; SE: 1157; E: -466; NE: 0.0144; N: -6.7104
[6 empty] | Predicted Source EUI (kBtu/ft2) | 235.9795
Reference Values
| Predicted Source EUI (kWh/m2) | 744.2383 | S: Based on EnergyStar Calculation, standardized operation
| Eref_nd (kWh/m2) | 118 | S: Based on 311 S Wacker, standardized operation
| Eref_del (kWh/m2) | 200 | S: Based on 311 S Wacker, standardized operation
| Eref_pri (kWh/m2) | 468.8701 | S: 80th Percentile of EnergyStar: Predicted * .63
THERMAL ENERGY DEMAND PERFORMANCE
| Heating Need |  | Total: Cooling Needs
| Month | QH,tr [kWh/m2] | QH,ve [kWh/m2] | QH,ht [kWh/m2] | QH,sol [kWh/m2] | QH,int,oc+ap [kWh/m2] | QH,int,li [kWh/m2] | QH,gn [kWh/m2] | ηH,ls | QH,nd [kWh/m2] |  | Month | QC,tr [kWh/m2] | QC,ve [kWh/m2] | QC,ht [kWh/m2] | QC,sol [kWh/m2] | QC,int,oc_ap [kWh/m2] | QC,int.li [kWh/m2] | QC,gn [kWh/m2] | ηC,ls | QC,nd [kWh/m2]
| Jan | 11.8624 | 3.6778 | 15.5402 | 1.9458 | 9.1251 | 2.1561 | 13.227 | 0.87943 | 3.9079 |  | Jan | 14.9326 | 4.649 | 19.5816 | 1.9458 | 9.1251 | 2.1561 | 13.227 | 0.63421 | 0.80827
| Feb | 9.7938 | 3.1579 | 12.9518 | 2.3216 | 8.242 | 1.9474 | 12.511 | 0.83408 | 2.5166 |  | Feb | 12.4982 | 4.0471 | 16.5452 | 2.3216 | 8.242 | 1.9474 | 12.511 | 0.69083 | 1.0811
| Mar | 7.9877 | 2.7919 | 10.7796 | 3.131 | 9.1251 | 2.1561 | 14.4122 | 0.68538 | 0.90181 |  | Mar | 10.5478 | 3.7019 | 14.2497 | 3.131 | 9.1251 | 2.1561 | 14.4122 | 0.8248 | 2.6591
| Apr | 5.3412 | 1.625 | 6.9662 | 3.3753 | 8.8308 | 2.0865 | 14.2926 | 0.4778 | 0.13717 |  | Apr | 7.1447 | 2.1808 | 9.3256 | 3.3753 | 8.8308 | 2.0865 | 14.2926 | 0.94535 | 5.4767
| May | 2.7452 | 0.64007 | 3.3853 | 4.4201 | 9.1251 | 2.1561 | 15.7013 | 0.21545 | 0.0024264 |  | May | 4.756 | 1.1133 | 5.8693 | 4.4201 | 9.1251 | 2.1561 | 15.7013 | 0.99293 | 9.8736
| Jun | -0.2555 | -0.077475 | -0.33298 | 4.4185 | 8.8308 | 2.0865 | 15.3358 | -0.021712 | 0 |  | Jun | 1.9673 | 0.60009 | 2.5674 | 4.4185 | 8.8308 | 2.0865 | 15.3358 | 0.99976 | 12.769
| Jul | -1.8272 | -0.48082 | -2.308 | 4.5797 | 9.1251 | 2.1561 | 15.8609 | -0.14552 | 0 |  | Jul | 0.55644 | 0.14586 | 0.7023 | 4.5797 | 9.1251 | 2.1561 | 15.8609 | 1 | 15.1586
| Aug | -0.61106 | -0.14534 | -0.7564 | 4.0296 | 9.1251 | 2.1561 | 15.3108 | -0.049403 | 0 |  | Aug | 1.688 | 0.40277 | 2.0907 | 4.0296 | 9.1251 | 2.1561 | 15.3108 | 0.9999 | 13.2203
| Sep | 1.2314 | 0.26231 | 1.4937 | 3.4804 | 8.8308 | 2.0865 | 14.3977 | 0.10374 | 4.3495e-05 |  | Sep | 3.2865 | 0.70344 | 3.9899 | 3.4804 | 8.8308 | 2.0865 | 14.3977 | 0.99792 | 10.4161
| Oct | 4.9699 | 1.4927 | 6.4627 | 2.9014 | 9.1251 | 2.1561 | 14.1826 | 0.44871 | 0.098831 |  | Oct | 6.8421 | 2.062 | 8.9041 | 2.9014 | 9.1251 | 2.1561 | 14.1826 | 0.95185 | 5.7072
| Nov | 7.2088 | 2.4225 | 9.6313 | 1.8111 | 8.8308 | 2.0865 | 12.7284 | 0.69116 | 0.83391 |  | Nov | 9.7495 | 3.2902 | 13.0397 | 1.8111 | 8.8308 | 2.0865 | 12.7284 | 0.81013 | 2.1646
| Dec | 11.3861 | 3.0878 | 14.4739 | 1.6832 | 9.1251 | 2.1561 | 12.9644 | 0.86221 | 3.2958 |  | Dec | 14.4315 | 3.9296 | 18.3611 | 1.6832 | 9.1251 | 2.1561 | 12.9644 | 0.65649 | 0.91054
| Total | 59.8328 | 18.4544 | 78.2872 | 38.0979 | 107.441 | 25.386 | 170.9249 | N/A | 11.6946 |  | Total | 88.4007 | 26.826 | 115.2267 | 38.0979 | 107.441 | 25.386 | 170.9249 | N/A | 80.245
| Heating Need |  | Total: Cooling Needs
| Month | QH,tr [MJ] | QH,ve [MJ] | QH,ht [MJ] | QH,sol [MJ] | QH,int,oc+ap [MJ] | QH,int,li [MJ] | QH,gn [MJ] | ηH,ls | QH,nd [MJ] |  | Month | QC,tr [MJ] | QC,ve [MJ] | QC,ht [MJ] | QC,sol [MJ] | QC,int,oc+ac [MJ] | QC,int,li [MJ] | QC,gn [MJ] | ηC,ls | QC,nd [MJ]
| Jan | 293423.9177 | 90971.4985 | 384395.4162 | 48131.633 | 225715.3655 | 53331.7156 | 327178.714 | 0.87943 | 96665.4705 |  | Jan | 369366.2114 | 114996.1012 | 484362.3126 | 48131.633 | 225715.3655 | 53331.7156 | 327178.714 | 0.63421 | 19993.0627
| Feb | 242256.2658 | 78113.7165 | 320369.9823 | 57425.6234 | 203871.943 | 48170.5818 | 309468.1482 | 0.83408 | 62249.1331 |  | Feb | 309149.8836 | 100106.7264 | 409256.61 | 57425.6234 | 203871.943 | 48170.5818 | 309468.1482 | 0.69083 | 26741.8515
| Mar | 197579.9545 | 69059.6798 | 266639.6342 | 77446.8104 | 225715.3655 | 53331.7156 | 356493.8914 | 0.68538 | 22306.779 |  | Mar | 260906.5296 | 91567.7576 | 352474.2872 | 77446.8104 | 225715.3655 | 53331.7156 | 356493.8914 | 0.8248 | 65773.9303
| Apr | 132117.6003 | 40195.8089 | 172313.4092 | 83490.3187 | 218434.2246 | 51611.3377 | 353535.8811 | 0.4778 | 3392.9152 |  | Apr | 176729.3639 | 53944.5477 | 230673.9116 | 83490.3187 | 218434.2246 | 51611.3377 | 353535.8811 | 0.94535 | 135469.2301
| May | 67903.8546 | 15832.545 | 83736.3995 | 109334.7922 | 225715.3655 | 53331.7156 | 388381.8733 | 0.21545 | 60.0179 |  | May | 117642.1168 | 27537.444 | 145179.5608 | 109334.7922 | 225715.3655 | 53331.7156 | 388381.8733 | 0.99293 | 244228.5487
| Jun | -6319.9998 | -1916.3989 | -8236.3988 | 109295.0487 | 218434.2246 | 51611.3377 | 379340.611 | -0.021712 | 0 |  | Jun | 48663.5252 | 14843.6522 | 63507.1774 | 109295.0487 | 218434.2246 | 51611.3377 | 379340.611 | 0.99976 | 315848.6717
| Jul | -45196.9488 | -11893.3986 | -57090.3474 | 113282.8215 | 225715.3655 | 53331.7156 | 392329.9026 | -0.14552 | 0 |  | Jul | 13763.9142 | 3607.8802 | 17371.7944 | 113282.8215 | 225715.3655 | 53331.7156 | 392329.9026 | 1 | 374958.1192
| Aug | -15114.9887 | -3595.1134 | -18710.1022 | 99674.7633 | 225715.3655 | 53331.7156 | 378721.8443 | -0.049403 | 0 |  | Aug | 41752.5738 | 9962.7536 | 51715.3275 | 99674.7633 | 225715.3655 | 53331.7156 | 378721.8443 | 0.9999 | 327011.5971
| Sep | 30458.8882 | 6488.5034 | 36947.3915 | 86090.5725 | 218434.2246 | 51611.3377 | 356136.1348 | 0.10374 | 1.0759 |  | Sep | 81293.3921 | 17400.0768 | 98693.4689 | 86090.5725 | 218434.2246 | 51611.3377 | 356136.1348 | 0.99792 | 257647.6309
| Oct | 122934.5889 | 36923.3493 | 159857.9383 | 71768.0365 | 225715.3655 | 53331.7156 | 350815.1176 | 0.44871 | 2444.6518 |  | Oct | 169244.1571 | 51004.1725 | 220248.3297 | 71768.0365 | 225715.3655 | 53331.7156 | 350815.1176 | 0.95185 | 141171.1725
| Nov | 178314.6384 | 59921.4558 | 238236.0942 | 44799.245 | 218434.2246 | 51611.3377 | 314844.8073 | 0.69116 | 20627.2189 |  | Nov | 241159.9724 | 81384.5563 | 322544.5287 | 44799.245 | 218434.2246 | 51611.3377 | 314844.8073 | 0.81013 | 53541.5386
| Dec | 281641.5849 | 76379.7555 | 358021.3404 | 41635.0893 | 225715.3655 | 53331.7156 | 320682.1703 | 0.86221 | 81524.6191 |  | Dec | 356971.9551 | 97201.709 | 454173.664 | 41635.0893 | 225715.3655 | 53331.7156 | 320682.1703 | 0.65649 | 22522.7954
| Total | 1479999.3559 | 456481.4016 | 1936480.7575 | 942374.7545 | 2657616.3999 | 627937.9416 | 4227929.096 | N/A | 289271.8813 |  | Total | 2186643.5953 | 663557.3776 | 2850200.9729 | 942374.7545 | 2657616.3999 | 627937.9416 | 4227929.096 | N/A | 1984908.1487
HEATING NEED
Note on D42: Author: Determined by building type.
Note on D43: Author: Determined by building type.
Note on J281: Author: Author: Minimum value 0.001 m3/h/m2 applied for the calculation

## Weather (hidden)
| Monthly Weather Data | [23 empty] | version 24Sep2010
|  |  |  | Select TMY or Year | TMY
| Monthly Averaged Data | [60 empty] | Averaged Solar Radiation on PV module(W/m2)
| M | Temp (deg C) | Wind Speed |  |  | Averaged solar radiation (W/m2) | [6 empty] | Dry Bulb Temperature (deg C) | [23 empty] | Global Horizontal Solar Radiation (W/m2) | [23 empty] | Tilt Angle | 0 | 30 | 30 | 30 | 30 | 30 | 45 | 45 | 45 | 45 | 45 | 60 | 60 | 60 | 60 | 60 | 90 | 90 | 90 | 90 | 90
|  |  |  | S | SE | E | NE | N | NW | W | SW | HOR. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Orientation |  | South | South-East | East | West | South-West | South | South-East | East | West | South-West | South | South-East | East | West | South-West | South | South-East | East | West | South-West | Humidity (g/kg dry air)
| Jan | -4.645 | 4.8803 | 125.2987 | 87.4701 | 43.0253 | 23.676 | 23.013 | 26.2917 | 58.8181 | 107.3479 | 73.5976 | -6.2839 | -6.1806 | -6.0871 | -6.2742 | -6.5226 | -6.8065 | -6.7806 | -6.5581 | -5.5516 | -4.3613 | -3.5452 | -2.7903 | -2.029 | -1.6839 | -1.5968 | -1.8613 | -2.9129 | -3.8258 | -4.5452 | -4.5097 | -4.7097 | -4.9774 | -5.2387 | -5.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3226 | 92.871 | 191.2258 | 260.129 | 302.7419 | 305.9032 | 276.7742 | 192.5161 | 98.8065 | 22.6774 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 68.7887 | 112.8956 | 71.7009 | 84.0855 | 55.7635 | 79.6492 | 127.7814 | 81.2821 | 82.1977 | 55.2651 | 87.7921 | 134.0206 | 87.0027 | 73.4542 | 55.4708 | 96.1174 | 114.6992 | 81.3552 | 25.8322 | 55.202 | 98.2782
| Feb | -2.5292 | 5.0704 | 143.2794 | 105.532 | 60.4409 | 34.6711 | 32.0986 | 40.1465 | 79.4993 | 127.1273 | 103.8899 | -3.6571 | -3.9286 | -4.1464 | -4.4643 | -4.9071 | -5.1214 | -5.2643 | -4.625 | -3.2929 | -2.0964 | -1.0214 | -0.24286 | 0.25714 | 0.39643 | 0.49643 | 0.26071 | -0.46429 | -1.425 | -2.3464 | -2.5821 | -2.85 | -2.925 | -3.15 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0714 | 48.25 | 149.5 | 271.3929 | 364.5 | 390.3929 | 395.1786 | 342.2857 | 273.9286 | 179.6429 | 67.6071 | 7.6071 | 0 | 0 | 0 | 0 | 0 | 0 |  | 93.1607 | 143.4939 | 79.0956 | 107.8192 | 85.3053 | 105.0974 | 158.3413 | 90.2892 | 105.8147 | 88.3912 | 113.671 | 161.9167 | 98.705 | 95.4145 | 87.2214 | 120.7804 | 130.8826 | 96.8192 | 34.6888 | 71.6222 | 114.7622
| Mar | 3.825 | 5.4858 | 146.2056 | 121.7475 | 84.7544 | 51.7841 | 42.8237 | 58.9952 | 99.9558 | 135.9106 | 143.3401 | 2.0226 | 1.8161 | 1.7677 | 1.2484 | 1.1323 | 0.91935 | 1.4226 | 2.7548 | 3.9677 | 5.0548 | 5.9387 | 6.8194 | 7.1871 | 7.3258 | 7.1935 | 6.7677 | 6.1355 | 5.0387 | 3.9419 | 3.3 | 2.9419 | 2.6097 | 2.3742 | 2.1194 | 0 | 0 | 0 | 0 | 0 | 0.58065 | 31.7742 | 132 | 241.4194 | 368.4839 | 455.5161 | 479.7097 | 503.9032 | 451.0968 | 361.0323 | 252.9032 | 128.0645 | 33.129 | 0.54839 | 0 | 0 | 0 | 0 | 0 |  | 125.1116 | 176.0594 | 97.1732 | 135.3224 | 106.6574 | 126.5799 | 186.525 | 105.0277 | 135.2626 | 109.6139 | 133.1982 | 182.5233 | 113.6992 | 124.7167 | 106.9895 | 134.8065 | 130.6444 | 111.5446 | 51.39 | 85.9274 | 117.9532
| Apr | 9.9386 | 4.8403 | 129.5457 | 123.9194 | 104.9122 | 71.359 | 54.1235 | 84.556 | 124.645 | 138.2998 | 183.0889 | 7.7933 | 7.6133 | 7.5633 | 7.1933 | 6.9567 | 7.0367 | 8.0933 | 9.2567 | 10.1867 | 10.9467 | 11.7933 | 12.2767 | 12.7633 | 13.12 | 13.0133 | 12.84 | 12.41 | 11.5033 | 10.5767 | 9.88 | 9.4867 | 9.18 | 8.9167 | 8.1267 | 0 | 0 | 0 | 0 | 0 | 7.1333 | 148.4 | 241.5333 | 371.5333 | 463.8 | 516.1 | 548.5333 | 519.5 | 528.9333 | 438.9333 | 327.9333 | 193.5667 | 85.5333 | 2.7 | 0 | 0 | 0 | 0 | 0 |  | 169.3958 | 211.6649 | 108.4646 | 150.0708 | 131.0079 | 147.2507 | 213.0351 | 109.5715 | 153.9881 | 136.1234 | 151.4974 | 196.9193 | 116.4101 | 146.5954 | 136.0158 | 148.9121 | 118.91 | 118.2833 | 80.6825 | 116.1468 | 126.8178
| May | 15.2972 | 3.7435 | 132.1856 | 143.7596 | 137.9482 | 102.3898 | 76.5605 | 119.7198 | 158.8442 | 155.6002 | 248.9946 | 10.7097 | 10.3161 | 10.1677 | 10.0516 | 9.8935 | 11.2258 | 13.5677 | 15.4742 | 17.2935 | 18.6968 | 19.8194 | 20.5806 | 21.0548 | 20.9452 | 20.5742 | 19.9871 | 19.5323 | 18.0968 | 16.0742 | 14.4871 | 13.3323 | 12.4548 | 11.7613 | 11.0355 | 0 | 0 | 0 | 0 | 8.7419 | 68.5484 | 202.2258 | 355.3226 | 507.2581 | 631.9032 | 680.7419 | 710.5806 | 723.9032 | 670.8065 | 538.2903 | 418.129 | 287.6452 | 135.7742 | 35.4194 | 0.58065 | 0 | 0 | 0 | 0 |  | 225.5228 | 256.0864 | 138.5135 | 166.9442 | 194.1601 | 191.6665 | 250.2974 | 134.9861 | 171.7999 | 199.2652 | 194.3341 | 223.3009 | 131.2122 | 164.6446 | 195.6136 | 186.683 | 119.6109 | 122.6935 | 119.3306 | 157.2135 | 150.4544
| Jun | 21.11 | 4.8865 | 121.0796 | 143.0968 | 148.0842 | 116.2031 | 87.9684 | 132.1614 | 164.7566 | 150.4755 | 262.2292 | 17.5967 | 17.2533 | 17.2067 | 16.8633 | 16.72 | 17.5933 | 19.5733 | 21.2833 | 22.5033 | 23.59 | 24.3833 | 24.83 | 25.2267 | 25.4667 | 25.39 | 25.1333 | 24.7567 | 23.9567 | 22.3333 | 20.68 | 19.41 | 18.79 | 18.1333 | 17.9667 | 0 | 0 | 0 | 0 | 16.2667 | 95.1 | 232.8333 | 384.4667 | 533.2 | 625.5 | 709.1 | 702.6333 | 698.3333 | 660.9 | 586.8667 | 475.2 | 319.9 | 185.6 | 61.7333 | 5.8667 | 0 | 0 | 0 | 0 |  | 249.375 | 266.9117 | 148.2385 | 180.0405 | 183.4378 | 161.6329 | 257.8768 | 143.0652 | 187.1282 | 189.5806 | 165.7667 | 226.7444 | 134.1764 | 181.4357 | 188.9822 | 165.4948 | 115.2961 | 130.4936 | 132.6923 | 165.1745 | 148.505
| Jul | 24.1296 | 4.2386 | 130.1293 | 142.6802 | 140.7194 | 109.4948 | 85.0596 | 129.5252 | 166.1474 | 158.3957 | 257.3656 | 20.7129 | 20.3419 | 19.871 | 19.7323 | 19.5323 | 20.7065 | 22.4 | 23.7323 | 24.9613 | 26.0774 | 27.0387 | 27.8323 | 28.4419 | 28.5774 | 28.4968 | 27.9806 | 27.3194 | 26.5161 | 25.4 | 24.0484 | 23.2452 | 22.6484 | 22.0419 | 21.4548 | 0 | 0 | 0 | 0 | 8.3871 | 67.5484 | 194.3226 | 338 | 477.0968 | 600.6129 | 664.3548 | 732.2903 | 761.3226 | 681.7097 | 611.1935 | 464.1613 | 333.0323 | 181.129 | 56.8065 | 4.8065 | 0 | 0 | 0 | 0 |  | 258.1747 | 289.4057 | 148.2151 | 189.7922 | 200.3488 | 187.655 | 279.9033 | 144.3842 | 197.6912 | 205.2651 | 189.893 | 246.8025 | 140.0819 | 192.0089 | 201.7196 | 182.8524 | 126.8283 | 143.1472 | 127.169 | 162.4508 | 153.6571
| Aug | 21.7804 | 3.8431 | 136.0947 | 138.7103 | 123.7441 | 88.1775 | 66.2563 | 103.4434 | 143.3642 | 150.8323 | 215.0591 | 18.5935 | 18.3194 | 18.1613 | 17.671 | 17.6645 | 18.029 | 20.0871 | 21.7097 | 23.2581 | 24.6032 | 25.2032 | 25.4323 | 25.9 | 25.7194 | 25.429 | 25.1742 | 24.5387 | 23.771 | 22.3645 | 21.4645 | 20.6 | 20.2742 | 19.5806 | 19.1806 | 0 | 0 | 0 | 0 | 0.32258 | 31.9355 | 138.4516 | 277.8065 | 413.3226 | 548.9677 | 611.0968 | 647.6129 | 624.2581 | 575.9032 | 489.1935 | 407.7097 | 253.0968 | 116.8065 | 24.7742 | 0.16129 | 0 | 0 | 0 | 0 |  | 223.8898 | 266.5429 | 128.6559 | 174.8463 | 178.2427 | 179.5597 | 264.3415 | 128.2886 | 179.6582 | 183.8016 | 185.5273 | 240.5806 | 134.3803 | 171.6644 | 181.1272 | 183.6255 | 139.097 | 138.145 | 105.0263 | 149.8421 | 157.4486
| Sep | 18.1421 | 3.4178 | 153.3054 | 136.1685 | 103.0097 | 62.644 | 47.8345 | 72.4894 | 118.8972 | 148.4966 | 174.6931 | 14.91 | 14.4867 | 14.14 | 13.88 | 13.7167 | 13.6067 | 15.5367 | 17.65 | 19.3933 | 20.46 | 21.4033 | 22.2433 | 22.8367 | 23.15 | 22.8867 | 22.4867 | 21.5567 | 19.96 | 18.6 | 17.8 | 16.8667 | 16.4967 | 15.8767 | 15.4667 | 0 | 0 | 0 | 0 | 0 | 10.9333 | 86.6333 | 219.0667 | 367.3667 | 479.5333 | 533.8333 | 555.5333 | 558.0333 | 500.5 | 398.0667 | 289.9 | 150.1 | 40.9667 | 2.1667 | 0 | 0 | 0 | 0 | 0 |  | 185.4375 | 241.8779 | 110.6299 | 156.4102 | 145.0591 | 158.1229 | 249.3672 | 117.7839 | 158.7987 | 151.9114 | 167.0214 | 237.7582 | 130.6122 | 149.3813 | 153.1545 | 172.2363 | 160.225 | 135.5426 | 77.7035 | 132.1623 | 163.427
| Oct | 10.9832 | 4.7862 | 153.0695 | 119.8451 | 74.1735 | 39.6366 | 34.5519 | 45.2912 | 87.7809 | 133.4038 | 122.5497 | 8.4968 | 8.229 | 8 | 7.8129 | 7.7968 | 7.5452 | 8.0613 | 9.8774 | 11.7548 | 13.1774 | 14.3258 | 14.9452 | 15.2484 | 15.429 | 15.3452 | 14.6387 | 13.2613 | 11.7645 | 11.0194 | 10.429 | 9.8419 | 9.3387 | 8.7419 | 8.5161 | 0 | 0 | 0 | 0 | 0 | 0.32258 | 33.3871 | 136.0645 | 265.0323 | 374.871 | 424.3548 | 427.9032 | 425.5161 | 378.1935 | 265.871 | 156.9677 | 48.9677 | 3.7419 | 0 | 0 | 0 | 0 | 0 | 0 |  | 117.9919 | 171.5023 | 94.0345 | 123.6167 | 108.4587 | 142.5193 | 185.5568 | 104.91 | 123.2698 | 110.8346 | 150.808 | 186.0942 | 114.2271 | 113.2778 | 108.5356 | 153.43 | 143.1756 | 112.0658 | 46.4651 | 87.176 | 128.1488
| Nov | 4.7393 | 5.2951 | 114.9026 | 84.5355 | 45.2516 | 26.5701 | 25.6212 | 28.7375 | 55.7373 | 97.38 | 75.7764 | 3.7133 | 3.4533 | 3.3567 | 3.3567 | 3.06 | 2.85 | 2.7533 | 3.4767 | 4.3433 | 5.4867 | 6.3133 | 6.9867 | 7.2433 | 7.3933 | 7.2733 | 6.6867 | 5.9233 | 5.2767 | 4.6333 | 4.2267 | 4.1533 | 4.08 | 3.8033 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7333 | 50.8667 | 146.3333 | 217.2667 | 286.4333 | 319 | 301.6 | 249.0333 | 160.8 | 70.1 | 12.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97.5361 | 159.9842 | 86.2662 | 108.2742 | 77.6876 | 114.324 | 180.2709 | 102.1456 | 106.1093 | 79.5311 | 124.3145 | 188.3199 | 113.6762 | 95.5797 | 79.1006 | 135.2338 | 161.5788 | 114.5156 | 30.5023 | 72.955 | 135.6304
| Dec | -3.677 | 4.2945 | 115.8563 | 82.5397 | 39.0707 | 19.7786 | 19.2697 | 21.3629 | 49.0963 | 95.2773 | 62.5826 | -4.8935 | -4.7839 | -4.9387 | -5.2387 | -5.2968 | -5.6452 | -5.6935 | -5.3516 | -4.4806 | -3.2129 | -2.1 | -1.4935 | -0.91935 | -0.70323 | -0.68387 | -1.471 | -2.4742 | -3.3129 | -3.6774 | -4.0226 | -4.1548 | -4.3677 | -4.5484 | -4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2258 | 98.7097 | 182.5806 | 252.129 | 262 | 262.4839 | 213.2903 | 143.871 | 59.7419 | 6.9677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 68.3987 | 120.3616 | 71.5695 | 80.0117 | 63.9226 | 103.6558 | 138.1749 | 84.1153 | 78.0408 | 64.8156 | 113.9689 | 146.8349 | 92.1646 | 69.7728 | 63.6251 | 119.583 | 130.8112 | 89.8624 | 21.5771 | 54.7786 | 109.2564
| Weather: |  | USA_IL_Chicago-Ohare.AP.725300_AMY 3
| Lat: |  | 41.78
| Lon: |  | -87.75
| Timezone: |  | -6
TMY/AMY Data for Chicago Ohare: | [5 empty] | Data computed using GIT weather convertor data sheet, TMY3 data from EnergyPlus, and AMY Data purchased from
Row | 1
Year (0=TMY) | Month | Avg Temp deg C | Wind Speed m/s | S Rad W/m2 | SE Rad W/m2 | E Rad W/m2 | NE Rad W/m2 | N Rad W/m2 | NW Rad W/m2 | W Rad W/m2 | SW Rad W/m2 | GHorz Rad W/m2 | Tdry deg C hr 1 | Tdry deg C hr 2 | Tdry deg C hr 3 | Tdry deg C hr 4 | Tdry deg C hr 5 | Tdry deg C hr 6 | Tdry deg C hr 7 | Tdry deg C hr 8 | Tdry deg C hr 9 | Tdry deg C hr 10 | Tdry deg C hr 11 | Tdry deg C hr 12 | Tdry deg C hr 13 | Tdry deg C hr 14 | Tdry deg C hr 15 | Tdry deg C hr 16 | Tdry deg C hr 17 | Tdry deg C hr 18 | Tdry deg C hr 19 | Tdry deg C hr 20 | Tdry deg C hr 21 | Tdry deg C hr 22 | Tdry deg C hr 23 | Tdry deg C hr 24 | GHorz W/m2 hr 1 | GHorz W/m2 hr 2 | GHorz W/m2 hr 3 | GHorz W/m2 hr 4 | GHorz W/m2 hr 5 | GHorz W/m2 hr 6 | GHorz W/m2 hr 7 | GHorz W/m2 hr 8 | GHorz W/m2 hr 9 | GHorz W/m2 hr 10 | GHorz W/m2 hr 11 | GHorz W/m2 hr 12 | GHorz W/m2 hr 13 | GHorz W/m2 hr 14 | GHorz W/m2 hr 15 | GHorz W/m2 hr 16 | GHorz W/m2 hr 17 | GHorz W/m2 hr 18 | GHorz W/m2 hr 19 | GHorz W/m2 hr 20 | GHorz W/m2 hr 21 | GHorz W/m2 hr 22 | GHorz W/m2 hr 23 | GHorz W/m2 hr 24
TMY | 1 | -4.645 | 4.8803 | 125.2987 | 87.4701 | 43.0253 | 23.676 | 23.013 | 26.2917 | 58.8181 | 107.3479 | 73.5976 | -6.2839 | -6.1806 | -6.0871 | -6.2742 | -6.5226 | -6.8065 | -6.7806 | -6.5581 | -5.5516 | -4.3613 | -3.5452 | -2.7903 | -2.029 | -1.6839 | -1.5968 | -1.8613 | -2.9129 | -3.8258 | -4.5452 | -4.5097 | -4.7097 | -4.9774 | -5.2387 | -5.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3226 | 92.871 | 191.2258 | 260.129 | 302.7419 | 305.9032 | 276.7742 | 192.5161 | 98.8065 | 22.6774 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TMY | 2 | -2.5292 | 5.0704 | 143.2794 | 105.532 | 60.4409 | 34.6711 | 32.0986 | 40.1465 | 79.4993 | 127.1273 | 103.8899 | -3.6571 | -3.9286 | -4.1464 | -4.4643 | -4.9071 | -5.1214 | -5.2643 | -4.625 | -3.2929 | -2.0964 | -1.0214 | -0.24286 | 0.25714 | 0.39643 | 0.49643 | 0.26071 | -0.46429 | -1.425 | -2.3464 | -2.5821 | -2.85 | -2.925 | -3.15 | -3.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0714 | 48.25 | 149.5 | 271.3929 | 364.5 | 390.3929 | 395.1786 | 342.2857 | 273.9286 | 179.6429 | 67.6071 | 7.6071 | 0 | 0 | 0 | 0 | 0 | 0
TMY | 3 | 3.825 | 5.4858 | 146.2056 | 121.7475 | 84.7544 | 51.7841 | 42.8237 | 58.9952 | 99.9558 | 135.9106 | 143.3401 | 2.0226 | 1.8161 | 1.7677 | 1.2484 | 1.1323 | 0.91935 | 1.4226 | 2.7548 | 3.9677 | 5.0548 | 5.9387 | 6.8194 | 7.1871 | 7.3258 | 7.1935 | 6.7677 | 6.1355 | 5.0387 | 3.9419 | 3.3 | 2.9419 | 2.6097 | 2.3742 | 2.1194 | 0 | 0 | 0 | 0 | 0 | 0.58065 | 31.7742 | 132 | 241.4194 | 368.4839 | 455.5161 | 479.7097 | 503.9032 | 451.0968 | 361.0323 | 252.9032 | 128.0645 | 33.129 | 0.54839 | 0 | 0 | 0 | 0 | 0
TMY | 4 | 9.9386 | 4.8403 | 129.5457 | 123.9194 | 104.9122 | 71.359 | 54.1235 | 84.556 | 124.645 | 138.2998 | 183.0889 | 7.7933 | 7.6133 | 7.5633 | 7.1933 | 6.9567 | 7.0367 | 8.0933 | 9.2567 | 10.1867 | 10.9467 | 11.7933 | 12.2767 | 12.7633 | 13.12 | 13.0133 | 12.84 | 12.41 | 11.5033 | 10.5767 | 9.88 | 9.4867 | 9.18 | 8.9167 | 8.1267 | 0 | 0 | 0 | 0 | 0 | 7.1333 | 148.4 | 241.5333 | 371.5333 | 463.8 | 516.1 | 548.5333 | 519.5 | 528.9333 | 438.9333 | 327.9333 | 193.5667 | 85.5333 | 2.7 | 0 | 0 | 0 | 0 | 0
TMY | 5 | 15.2972 | 3.7435 | 132.1856 | 143.7596 | 137.9482 | 102.3898 | 76.5605 | 119.7198 | 158.8442 | 155.6002 | 248.9946 | 10.7097 | 10.3161 | 10.1677 | 10.0516 | 9.8935 | 11.2258 | 13.5677 | 15.4742 | 17.2935 | 18.6968 | 19.8194 | 20.5806 | 21.0548 | 20.9452 | 20.5742 | 19.9871 | 19.5323 | 18.0968 | 16.0742 | 14.4871 | 13.3323 | 12.4548 | 11.7613 | 11.0355 | 0 | 0 | 0 | 0 | 8.7419 | 68.5484 | 202.2258 | 355.3226 | 507.2581 | 631.9032 | 680.7419 | 710.5806 | 723.9032 | 670.8065 | 538.2903 | 418.129 | 287.6452 | 135.7742 | 35.4194 | 0.58065 | 0 | 0 | 0 | 0
TMY | 6 | 21.11 | 4.8865 | 121.0796 | 143.0968 | 148.0842 | 116.2031 | 87.9684 | 132.1614 | 164.7566 | 150.4755 | 262.2292 | 17.5967 | 17.2533 | 17.2067 | 16.8633 | 16.72 | 17.5933 | 19.5733 | 21.2833 | 22.5033 | 23.59 | 24.3833 | 24.83 | 25.2267 | 25.4667 | 25.39 | 25.1333 | 24.7567 | 23.9567 | 22.3333 | 20.68 | 19.41 | 18.79 | 18.1333 | 17.9667 | 0 | 0 | 0 | 0 | 16.2667 | 95.1 | 232.8333 | 384.4667 | 533.2 | 625.5 | 709.1 | 702.6333 | 698.3333 | 660.9 | 586.8667 | 475.2 | 319.9 | 185.6 | 61.7333 | 5.8667 | 0 | 0 | 0 | 0
TMY | 7 | 24.1296 | 4.2386 | 130.1293 | 142.6802 | 140.7194 | 109.4948 | 85.0596 | 129.5252 | 166.1474 | 158.3957 | 257.3656 | 20.7129 | 20.3419 | 19.871 | 19.7323 | 19.5323 | 20.7065 | 22.4 | 23.7323 | 24.9613 | 26.0774 | 27.0387 | 27.8323 | 28.4419 | 28.5774 | 28.4968 | 27.9806 | 27.3194 | 26.5161 | 25.4 | 24.0484 | 23.2452 | 22.6484 | 22.0419 | 21.4548 | 0 | 0 | 0 | 0 | 8.3871 | 67.5484 | 194.3226 | 338 | 477.0968 | 600.6129 | 664.3548 | 732.2903 | 761.3226 | 681.7097 | 611.1935 | 464.1613 | 333.0323 | 181.129 | 56.8065 | 4.8065 | 0 | 0 | 0 | 0
TMY | 8 | 21.7804 | 3.8431 | 136.0947 | 138.7103 | 123.7441 | 88.1775 | 66.2563 | 103.4434 | 143.3642 | 150.8323 | 215.0591 | 18.5935 | 18.3194 | 18.1613 | 17.671 | 17.6645 | 18.029 | 20.0871 | 21.7097 | 23.2581 | 24.6032 | 25.2032 | 25.4323 | 25.9 | 25.7194 | 25.429 | 25.1742 | 24.5387 | 23.771 | 22.3645 | 21.4645 | 20.6 | 20.2742 | 19.5806 | 19.1806 | 0 | 0 | 0 | 0 | 0.32258 | 31.9355 | 138.4516 | 277.8065 | 413.3226 | 548.9677 | 611.0968 | 647.6129 | 624.2581 | 575.9032 | 489.1935 | 407.7097 | 253.0968 | 116.8065 | 24.7742 | 0.16129 | 0 | 0 | 0 | 0
TMY | 9 | 18.1421 | 3.4178 | 153.3054 | 136.1685 | 103.0097 | 62.644 | 47.8345 | 72.4894 | 118.8972 | 148.4966 | 174.6931 | 14.91 | 14.4867 | 14.14 | 13.88 | 13.7167 | 13.6067 | 15.5367 | 17.65 | 19.3933 | 20.46 | 21.4033 | 22.2433 | 22.8367 | 23.15 | 22.8867 | 22.4867 | 21.5567 | 19.96 | 18.6 | 17.8 | 16.8667 | 16.4967 | 15.8767 | 15.4667 | 0 | 0 | 0 | 0 | 0 | 10.9333 | 86.6333 | 219.0667 | 367.3667 | 479.5333 | 533.8333 | 555.5333 | 558.0333 | 500.5 | 398.0667 | 289.9 | 150.1 | 40.9667 | 2.1667 | 0 | 0 | 0 | 0 | 0
TMY | 10 | 10.9832 | 4.7862 | 153.0695 | 119.8451 | 74.1735 | 39.6366 | 34.5519 | 45.2912 | 87.7809 | 133.4038 | 122.5497 | 8.4968 | 8.229 | 8 | 7.8129 | 7.7968 | 7.5452 | 8.0613 | 9.8774 | 11.7548 | 13.1774 | 14.3258 | 14.9452 | 15.2484 | 15.429 | 15.3452 | 14.6387 | 13.2613 | 11.7645 | 11.0194 | 10.429 | 9.8419 | 9.3387 | 8.7419 | 8.5161 | 0 | 0 | 0 | 0 | 0 | 0.32258 | 33.3871 | 136.0645 | 265.0323 | 374.871 | 424.3548 | 427.9032 | 425.5161 | 378.1935 | 265.871 | 156.9677 | 48.9677 | 3.7419 | 0 | 0 | 0 | 0 | 0 | 0
TMY | 11 | 4.7393 | 5.2951 | 114.9026 | 84.5355 | 45.2516 | 26.5701 | 25.6212 | 28.7375 | 55.7373 | 97.38 | 75.7764 | 3.7133 | 3.4533 | 3.3567 | 3.3567 | 3.06 | 2.85 | 2.7533 | 3.4767 | 4.3433 | 5.4867 | 6.3133 | 6.9867 | 7.2433 | 7.3933 | 7.2733 | 6.6867 | 5.9233 | 5.2767 | 4.6333 | 4.2267 | 4.1533 | 4.08 | 3.8033 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7333 | 50.8667 | 146.3333 | 217.2667 | 286.4333 | 319 | 301.6 | 249.0333 | 160.8 | 70.1 | 12.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TMY | 12 | -3.677 | 4.2945 | 115.8563 | 82.5397 | 39.0707 | 19.7786 | 19.2697 | 21.3629 | 49.0963 | 95.2773 | 62.5826 | -4.8935 | -4.7839 | -4.9387 | -5.2387 | -5.2968 | -5.6452 | -5.6935 | -5.3516 | -4.4806 | -3.2129 | -2.1 | -1.4935 | -0.91935 | -0.70323 | -0.68387 | -1.471 | -2.4742 | -3.3129 | -3.6774 | -4.0226 | -4.1548 | -4.3677 | -4.5484 | -4.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.2258 | 98.7097 | 182.5806 | 252.129 | 262 | 262.4839 | 213.2903 | 143.871 | 59.7419 | 6.9677 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 1 | -3.804 | 4.204 | 130.8778 | 89.5216 | 43.8854 | 21.8267 | 21.2207 | 25.474 | 63.0148 | 113.0802 | 73.9098 | -4.8968 | -4.7968 | -4.9806 | -5.1774 | -5.3871 | -5.3516 | -5.5258 | -5.229 | -4.4968 | -3.4968 | -2.5258 | -1.9742 | -1.6419 | -1.5 | -1.6548 | -2.0065 | -2.7 | -3.1645 | -3.5581 | -3.7903 | -4.1677 | -4.3484 | -4.471 | -4.4767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1935 | 122.8065 | 189.1613 | 250.6774 | 298.3226 | 289.3226 | 262.2581 | 218.7097 | 122.1613 | 14.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 2 | -2.9549 | 4.6747 | 148.4752 | 105.4627 | 59.6017 | 32.5709 | 29.112 | 39.2118 | 85.6116 | 135.7109 | 108.3065 | -3.4464 | -3.7857 | -4.0786 | -4.1536 | -4.3893 | -4.4607 | -4.625 | -4.3286 | -3.8714 | -3.1964 | -2.5393 | -1.925 | -1.5643 | -1.0857 | -1.1393 | -1.3143 | -1.7071 | -2.1929 | -2.4357 | -2.6321 | -2.7286 | -2.9607 | -3.1429 | -3.2143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.7857 | 175.6786 | 243.25 | 322.6786 | 394.5 | 416.2857 | 396 | 301.2857 | 202.25 | 84.9643 | 0.67857 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 3 | 1.2546 | 4.6526 | 157.9685 | 132.7209 | 92.9038 | 54.1428 | 43.6856 | 65.3908 | 112.522 | 149.0797 | 156.5255 | -0.98387 | -1.2065 | -1.4871 | -1.6613 | -1.9161 | -2.1355 | -1.5258 | -0.21613 | 1.0968 | 2.1419 | 3.1 | 3.9065 | 4.4065 | 4.9161 | 5.0065 | 4.8516 | 4.1258 | 3.1 | 2.2258 | 1.429 | 0.99677 | 0.39355 | 0.087097 | -0.54194 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2903 | 188.4839 | 292.9355 | 416.2903 | 501.4194 | 507.6129 | 490.2581 | 463.9355 | 392.7742 | 275.7742 | 164.5806 | 35.2581 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 4 | 11.5481 | 5.0606 | 149.6666 | 138.8103 | 115.1376 | 77.149 | 58.7839 | 96.7105 | 146.5027 | 163.214 | 215.1611 | 8.2467 | 8.3833 | 8.0567 | 7.7867 | 7.6367 | 8.17 | 9.22 | 10.4833 | 11.6433 | 12.85 | 13.8167 | 14.81 | 15.61 | 16.0267 | 16.1667 | 15.8333 | 15.1133 | 13.91 | 12.4833 | 11.46 | 10.7667 | 10.1467 | 9.7567 | 8.7767 | 0 | 0 | 0 | 0 | 0 | 9.9333 | 137.1333 | 268.6667 | 402.4333 | 524.8667 | 619.9 | 644.6333 | 682.9 | 625.9333 | 520.3 | 382.1333 | 241.8 | 100.0333 | 3.2 | 0 | 0 | 0 | 0 | 0
2001 | 5 | 15.9392 | 4.1325 | 121.4338 | 132.3503 | 128.5001 | 98.7709 | 77.5097 | 115.984 | 148.4423 | 143.0383 | 216.7581 | 13.2452 | 12.9839 | 12.7645 | 12.4839 | 12.1548 | 13.2032 | 14.6258 | 16.1613 | 17.3613 | 18.1161 | 18.7742 | 19.2258 | 19.4484 | 19.5645 | 19.2903 | 19.0129 | 18.4065 | 17.6903 | 16.4387 | 15.3645 | 14.9129 | 14.1871 | 13.5968 | 13.529 | 0 | 0 | 0 | 0 | 0.70968 | 87.0645 | 200.0968 | 333.4194 | 443.2581 | 554.2903 | 563.6129 | 588.2258 | 569.9677 | 537.4194 | 492.5484 | 396.3226 | 256.2581 | 143.3871 | 35.6129 | 0 | 0 | 0 | 0 | 0
2001 | 6 | 20.2236 | 3.3981 | 114.5807 | 130.7865 | 135.0233 | 108.0386 | 86.2926 | 133.4961 | 166.1911 | 149.2182 | 247.4639 | 16.7833 | 16.4267 | 16.04 | 15.4567 | 15.6233 | 17.1133 | 18.83 | 20.0433 | 20.96 | 21.95 | 22.7133 | 23.4033 | 24.02 | 24.11 | 24.3467 | 24.2233 | 23.8333 | 23.17 | 22.1567 | 20.7867 | 19.6567 | 18.45 | 18.1767 | 17.0933 | 0 | 0 | 0 | 0 | 4.1 | 99.6333 | 214.5 | 335.6 | 444.7 | 555.4333 | 614.6667 | 661.4333 | 664.1667 | 656.9667 | 591.7333 | 495.4333 | 343.2 | 188.9333 | 68.6333 | 0 | 0 | 0 | 0 | 0
2001 | 7 | 23.8907 | 3.3011 | 125.2695 | 138.7586 | 136.1491 | 104.3192 | 80.6109 | 124.7797 | 160.0867 | 152.0335 | 254.3911 | 20.8452 | 20.4419 | 20.2871 | 19.8742 | 19.9129 | 21.0161 | 22.4387 | 23.6677 | 24.9516 | 26.2548 | 26.7581 | 27.3419 | 27.8355 | 27.8484 | 27.7226 | 27.4387 | 26.9194 | 26.2323 | 25.0323 | 23.6419 | 22.8387 | 21.9 | 21.2613 | 20.9161 | 0 | 0 | 0 | 0 | 0.51613 | 77.4516 | 198.9677 | 343.9032 | 481.0968 | 600.3871 | 704.1935 | 740.2903 | 719.7742 | 661.2581 | 572.0968 | 458.3871 | 313.2903 | 173.7097 | 60.0645 | 0 | 0 | 0 | 0 | 0
2001 | 8 | 23.0191 | 3.3363 | 137.2556 | 137.1364 | 120.7511 | 85.0401 | 64.3004 | 101.5129 | 143.0239 | 151.8099 | 216.6008 | 20.5484 | 20.1355 | 19.9871 | 19.6871 | 19.4935 | 20.0194 | 21.2548 | 22.8323 | 23.829 | 24.6065 | 25.5226 | 25.9484 | 26.5581 | 26.6935 | 26.7226 | 26.4839 | 25.9484 | 25.0452 | 23.9065 | 22.4806 | 21.8548 | 21.2677 | 20.9387 | 20.6935 | 0 | 0 | 0 | 0 | 0 | 14.5484 | 150.2903 | 305.4516 | 406.4194 | 517.4194 | 620.6129 | 635.7742 | 652.1613 | 607.8065 | 510.3226 | 382.6129 | 254.4516 | 125.8065 | 14.7419 | 0 | 0 | 0 | 0 | 0
2001 | 9 | 16.9306 | 3.7282 | 152.0177 | 131.0707 | 98.0054 | 59.8023 | 46.2566 | 73.5937 | 122.8491 | 152.2398 | 174.5875 | 14.4133 | 14.19 | 14.1433 | 13.71 | 13.6633 | 13.7533 | 15.09 | 16.4633 | 17.78 | 18.85 | 19.7467 | 20.2 | 20.81 | 20.6967 | 20.5933 | 20.2833 | 19.4633 | 18.2733 | 16.8767 | 16.28 | 15.7433 | 15.4233 | 15.0067 | 14.88 | 0 | 0 | 0 | 0 | 0 | 0.96667 | 93.4 | 223.9667 | 348.2333 | 458.4 | 557.0667 | 533.8 | 575.0667 | 489.2667 | 416.8 | 300.2 | 161.2333 | 31.7 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 10 | 11.3519 | 4.6276 | 128.6595 | 99.1413 | 60.8909 | 34.9431 | 31.3633 | 40.0635 | 75.1645 | 114.1642 | 106.2863 | 9.5742 | 9.4065 | 9.0935 | 8.8484 | 8.6645 | 8.5645 | 8.8032 | 10.0935 | 11.3161 | 12.5677 | 13.571 | 14.0806 | 14.6355 | 14.5 | 14.4774 | 14.0935 | 13.3871 | 12.3161 | 11.7774 | 11.3484 | 10.7419 | 10.4516 | 10.329 | 9.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 12.4516 | 125.6774 | 220.129 | 323.0645 | 377.9032 | 385.9355 | 369.6774 | 326.4516 | 233.9355 | 134.7097 | 40.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 11 | 9.3604 | 4.1986 | 131.7757 | 90.6405 | 45.1509 | 23.7437 | 22.7431 | 27.563 | 65.1394 | 115.2048 | 82.0264 | 8.0367 | 7.6967 | 7.48 | 7.1033 | 6.9833 | 6.61 | 6.2767 | 7.42 | 8.7833 | 10.13 | 11.22 | 12.05 | 12.57 | 12.8 | 12.6667 | 11.9467 | 10.9233 | 10.11 | 9.83 | 9.5167 | 9.0033 | 8.96 | 8.2467 | 8.2867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.1333 | 162.2333 | 240.6 | 310.9333 | 323.9 | 325 | 265.9 | 196.6667 | 84.5333 | 1.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2001 | 12 | 1.037 | 4.3078 | 108.3529 | 75.9731 | 35.8156 | 19.3238 | 19.0256 | 20.8822 | 47.194 | 90.6429 | 59.851 | 0.087097 | 0.051613 | -0.25484 | -0.40323 | -0.69355 | -0.78065 | -0.98387 | -0.77097 | 0.19355 | 1.2968 | 2.2935 | 2.8839 | 3.4677 | 3.6 | 3.4065 | 2.8129 | 2.1387 | 1.6935 | 1.4355 | 1.1871 | 1.0484 | 0.82258 | 0.28387 | 0.10312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1613 | 109.6452 | 180.6774 | 235.1613 | 252.0968 | 257.1935 | 197.6129 | 144.0968 | 59.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 1 | -0.032705 | 4.5965 | 140.1993 | 94.2773 | 43.6373 | 22.1888 | 21.5863 | 25.3323 | 64.8183 | 121.2069 | 78.7981 | -1.1129 | -1.5387 | -1.8516 | -2.1 | -2.3452 | -2.6387 | -2.6645 | -2.2935 | -1.2161 | -0.19032 | 0.91935 | 1.7 | 2.4355 | 2.8516 | 2.9581 | 2.4935 | 1.7968 | 1.2613 | 0.78387 | 0.43548 | 0.22258 | 0.029032 | -0.25161 | -0.48333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5806 | 114.7742 | 204.9355 | 283.7742 | 309 | 334.3548 | 286.4516 | 221.7097 | 115.4516 | 12.5806 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 2 | 0.21815 | 5.3051 | 156.2123 | 116.0567 | 65.1497 | 33.457 | 29.9638 | 39.4123 | 83.3881 | 135.9842 | 111.4762 | -0.63214 | -0.90714 | -1.275 | -1.725 | -1.9214 | -2.1607 | -2.3071 | -1.8643 | -0.775 | 0.23929 | 1.2286 | 1.8786 | 2.3679 | 2.825 | 3.0464 | 2.7821 | 2.0964 | 1.4321 | 0.87143 | 0.58214 | 0.11429 | -0.025 | -0.29643 | -0.33929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.3571 | 194.6429 | 292.4286 | 369.5714 | 404.9286 | 420.8571 | 366.8929 | 284.1071 | 195.75 | 81.3929 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 3 | 1.3043 | 5.2337 | 158.5073 | 130.2266 | 89.1404 | 53.6295 | 43.8064 | 66.1466 | 113.8024 | 152.469 | 157.8763 | -0.070968 | -0.42581 | -0.78387 | -0.78387 | -1.0742 | -1.2129 | -0.96774 | 0.029032 | 1.0935 | 1.7968 | 2.6129 | 2.9613 | 3.5323 | 3.8355 | 3.9903 | 3.8581 | 3.4194 | 2.5968 | 1.8484 | 1.5452 | 1.3226 | 1.0581 | 0.81613 | 0.30645 | 0 | 0 | 0 | 0 | 0 | 0 | 23.1613 | 178.8065 | 278.7419 | 377.8065 | 490.5806 | 552.2903 | 536.871 | 463.9677 | 400.0968 | 291.4516 | 159.2581 | 36 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 4 | 9.9419 | 4.8293 | 129.5457 | 123.9194 | 104.9122 | 71.359 | 54.1235 | 84.556 | 124.645 | 138.2998 | 183.0889 | 7.8233 | 7.6133 | 7.5733 | 7.1933 | 6.9567 | 7.0367 | 8.0933 | 9.2567 | 10.1867 | 10.9467 | 11.7933 | 12.2767 | 12.7633 | 13.12 | 13.0133 | 12.84 | 12.41 | 11.5033 | 10.5767 | 9.88 | 9.4867 | 9.1667 | 8.93 | 8.1667 | 0 | 0 | 0 | 0 | 0 | 7.1333 | 148.4 | 241.5333 | 371.5333 | 463.8 | 516.1 | 548.5333 | 519.5 | 528.9333 | 438.9333 | 327.9333 | 193.5667 | 85.5333 | 2.7 | 0 | 0 | 0 | 0 | 0
2002 | 5 | 13.0138 | 4.6117 | 118.141 | 125.4189 | 120.5834 | 92.4189 | 73.2552 | 113.8232 | 148.3393 | 142.9708 | 216.7849 | 10.9323 | 10.6065 | 10.2032 | 9.7677 | 9.3613 | 10.2871 | 11.5258 | 12.6581 | 13.6 | 14.4258 | 14.8226 | 15.3774 | 16.0194 | 16.2194 | 16.1 | 15.9774 | 15.5581 | 14.9097 | 13.9065 | 12.9419 | 12.2645 | 12.0323 | 11.7613 | 11.0742 | 0 | 0 | 0 | 0 | 0.74194 | 84.129 | 185.0645 | 287.3226 | 424.3548 | 502.2581 | 590.2581 | 607.129 | 613.6129 | 581.9355 | 469.0645 | 404.8387 | 276.6452 | 140.3871 | 35.0968 | 0 | 0 | 0 | 0 | 0
2002 | 6 | 21.7272 | 3.39 | 116.9967 | 134.0503 | 138.435 | 110.3065 | 85.4628 | 125.4398 | 156.8486 | 144.7553 | 247.3125 | 18.4767 | 18.19 | 18.04 | 17.7 | 17.74 | 18.7 | 20.24 | 21.6933 | 22.6567 | 23.6267 | 24.4933 | 24.6333 | 25.3267 | 25.5567 | 25.7367 | 25.7467 | 25.0067 | 24.33 | 22.8933 | 21.8 | 20.7733 | 19.83 | 19.4567 | 18.8067 | 0 | 0 | 0 | 0 | 4.2333 | 102.5667 | 225.7333 | 351.4667 | 487.7 | 562.0667 | 633.5 | 664.3333 | 703.2333 | 659.4 | 547.1 | 459.8667 | 291.8667 | 177.6667 | 64.7667 | 0 | 0 | 0 | 0 | 0
2002 | 7 | 25.4165 | 3.5782 | 127.4972 | 143.3943 | 142.6495 | 109.7419 | 84.0589 | 130.1989 | 166.4714 | 156.4557 | 258.3777 | 22.1516 | 21.9419 | 21.771 | 21.2774 | 21.1968 | 22.3774 | 24.0871 | 25.3194 | 26.3645 | 27.3581 | 28.0097 | 28.7129 | 29.0065 | 29.2645 | 29.3871 | 29.1387 | 28.6806 | 27.9161 | 26.7065 | 25.5581 | 24.371 | 23.8065 | 22.9548 | 22.6387 | 0 | 0 | 0 | 0 | 0.54839 | 75.3548 | 219.0968 | 356.2581 | 508.0968 | 625.5161 | 662.0323 | 699.7097 | 695.0645 | 679.1935 | 598.0645 | 500.6774 | 333 | 189.2903 | 59.1613 | 0 | 0 | 0 | 0 | 0
2002 | 8 | 23.1802 | 3.3665 | 140.3926 | 139.0573 | 122.9171 | 87.0348 | 65.7451 | 107.2204 | 152.1701 | 159.918 | 223.957 | 20.2032 | 20.0871 | 19.929 | 19.4581 | 19.1323 | 20 | 21.3161 | 22.7129 | 23.9258 | 24.9355 | 25.8968 | 26.6774 | 26.9548 | 26.9677 | 26.9677 | 26.6677 | 26.0032 | 25.0903 | 24 | 22.9968 | 22.4194 | 21.8355 | 21.3097 | 20.8387 | 0 | 0 | 0 | 0 | 0 | 15.4516 | 157.0645 | 291.5806 | 432.3871 | 524.3871 | 607.2258 | 658.9677 | 656.3226 | 642 | 549.0645 | 423.0645 | 273.871 | 126.2581 | 17.3226 | 0 | 0 | 0 | 0 | 0
2002 | 9 | 20.0324 | 3.1592 | 164.1843 | 140.778 | 104.6162 | 64.1149 | 49.0681 | 78.1746 | 131.635 | 164.6953 | 187.9139 | 16.61 | 16.1167 | 15.84 | 15.5467 | 15.1667 | 15.19 | 17.49 | 19.18 | 20.74 | 22.1233 | 23.1533 | 24.0133 | 24.9033 | 25.2933 | 25.0567 | 24.6333 | 23.6533 | 22.2467 | 20.89 | 20.0033 | 19.4867 | 18.6533 | 17.8367 | 16.95 | 0 | 0 | 0 | 0 | 0 | 1.1 | 98.9667 | 230 | 361.1 | 493.4333 | 587.4333 | 618.9333 | 590.9 | 563.5333 | 441.4 | 312.2667 | 173.4 | 37.4667 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 10 | 9.8004 | 4.0292 | 138.7084 | 103.0754 | 62.4851 | 35.9274 | 32.4139 | 44.0432 | 85.8226 | 127.902 | 114.8616 | 8.2742 | 7.929 | 7.8 | 7.7935 | 7.6581 | 7.5097 | 7.9839 | 8.9613 | 9.9645 | 11.0806 | 11.6581 | 12.2548 | 12.6839 | 12.9742 | 12.7774 | 12.4032 | 11.2935 | 10.4613 | 10.0452 | 9.4839 | 9.1968 | 8.4065 | 8.0742 | 8.5419 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6129 | 138.5484 | 220.6452 | 312.9677 | 386.7097 | 423.9355 | 416.1613 | 357.2581 | 272.7419 | 167.7419 | 47.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 11 | 3.479 | 4.4193 | 106.8619 | 77.8661 | 41.8784 | 24.8932 | 23.9986 | 27.5074 | 53.6764 | 92.0744 | 70.875 | 2.54 | 2.29 | 1.9267 | 1.65 | 1.3933 | 1.4267 | 1.32 | 2.09 | 3.09 | 4.1367 | 4.8533 | 5.5 | 5.9467 | 5.97 | 5.8033 | 5.3667 | 4.78 | 4.3133 | 3.83 | 3.57 | 3.26 | 2.9233 | 2.7233 | 2.7933 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13333 | 50.5333 | 143.8 | 233.1 | 272.4 | 275.5333 | 282.6667 | 214.5 | 151.4667 | 75.1667 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2002 | 12 | -0.85181 | 4.5875 | 113.6448 | 77.6435 | 35.7283 | 18.5574 | 18.2802 | 20.4443 | 50.1795 | 96.3268 | 60.7664 | -1.8839 | -2.2806 | -2.2645 | -2.4613 | -2.6484 | -2.6516 | -2.771 | -2.4161 | -1.4935 | -0.66774 | 0.070968 | 0.80968 | 1.2742 | 1.5935 | 1.529 | 1.0774 | 0.53871 | -0.03871 | -0.32581 | -0.59032 | -0.78387 | -1.0226 | -1.3484 | -1.6625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8387 | 112.9677 | 177.1613 | 234.5806 | 252.0645 | 251.8065 | 209.6774 | 153.2258 | 67.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 1 | -5.8633 | 4.9443 | 155.0274 | 107.1499 | 49.4504 | 23.1073 | 22.3299 | 26.8625 | 68.6898 | 130.7385 | 84.074 | -6.5355 | -6.9516 | -7.1548 | -7.4935 | -7.629 | -8.071 | -8.2871 | -8.0935 | -7.2903 | -6.4258 | -5.4645 | -4.7806 | -4.0742 | -3.5935 | -3.5129 | -3.6742 | -4.1903 | -4.4516 | -4.7871 | -5.0774 | -5.4097 | -5.6581 | -5.8968 | -6.2267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8387 | 135.9677 | 212.9677 | 313.8387 | 350.9355 | 351.0645 | 281.8065 | 222.0968 | 128.1613 | 14.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 2 | -4.4799 | 4.8223 | 157.6674 | 114.9169 | 65.9073 | 34.5339 | 31.1616 | 41.4371 | 88.8538 | 140.5648 | 114.5714 | -5.7714 | -5.9786 | -6.4464 | -6.65 | -6.9464 | -7.2964 | -7.4571 | -6.4214 | -5.4321 | -4.175 | -3.4286 | -2.6 | -1.9607 | -1.475 | -1.3393 | -1.6071 | -2.1643 | -2.9643 | -3.4571 | -4.1321 | -4.525 | -4.7571 | -5.2143 | -5.3179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.1429 | 195.2143 | 292.6786 | 377.8929 | 405.8214 | 411 | 390.7143 | 325.4643 | 206.4643 | 84.75 | 0.57143 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 3 | 2.8828 | 4.3155 | 144.9732 | 119.5157 | 83.2076 | 51.3627 | 42.1953 | 61.7418 | 104.8506 | 139.5617 | 146.3172 | 0.76774 | 0.29032 | 0.21613 | -0.051613 | -0.19355 | -0.10323 | 0.34516 | 1.6226 | 2.6581 | 3.6258 | 4.8032 | 5.6452 | 6.2871 | 6.1355 | 6.0548 | 5.8968 | 5.6 | 4.5452 | 3.7129 | 3.1452 | 2.5677 | 2.4 | 1.9871 | 1.229 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9677 | 171.4839 | 256.2258 | 341 | 433.4516 | 523.6452 | 525.871 | 444.9032 | 345.6452 | 257.0323 | 149.5484 | 35.8387 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 4 | 8.7987 | 4.7953 | 136.7343 | 130.9118 | 109.7633 | 73.9856 | 55.271 | 87.0156 | 129.1433 | 144.9465 | 193.2014 | 6.3533 | 6.2267 | 5.8133 | 5.0867 | 4.92 | 5.2467 | 6.52 | 8.11 | 9.65 | 10.9333 | 12.0933 | 12.39 | 12.9467 | 12.82 | 12.6433 | 12.2533 | 11.1833 | 10.0133 | 8.94 | 8.1667 | 7.6833 | 7.55 | 6.9633 | 6.6633 | 0 | 0 | 0 | 0 | 0 | 6.2 | 142.7667 | 266.3667 | 385.5 | 477.3667 | 564 | 595.5333 | 625.5333 | 540.5667 | 412.4333 | 320.5667 | 211.5333 | 85.9667 | 2.5 | 0 | 0 | 0 | 0 | 0
2003 | 5 | 13.3171 | 4.5805 | 119.9078 | 122.4458 | 116.7207 | 89.7315 | 72.7196 | 116.7385 | 155.0652 | 149.4367 | 226.1075 | 10.7032 | 10.4355 | 10.371 | 10.2323 | 10.2806 | 11.0355 | 12.1839 | 13.0677 | 14.1 | 14.8226 | 15.6194 | 16.4774 | 16.8613 | 17.3194 | 17.1645 | 16.4419 | 15.8419 | 15 | 13.7452 | 12.5871 | 11.9645 | 11.4935 | 10.9129 | 10.9484 | 0 | 0 | 0 | 0 | 0.67742 | 86.5806 | 187.0323 | 285.7742 | 402.9355 | 496.0323 | 572.2258 | 643.9355 | 668.5161 | 633.9677 | 571.2258 | 409.9355 | 289.129 | 143 | 35.6129 | 0 | 0 | 0 | 0 | 0
2003 | 6 | 18.9111 | 3.4744 | 120.2562 | 135.966 | 138.7095 | 109.2797 | 86.0926 | 133.1942 | 167.9347 | 153.287 | 263.1903 | 14.8067 | 14.5867 | 14.2 | 14 | 14.1033 | 15.9267 | 17.6567 | 19.15 | 20.5067 | 21.55 | 22.3533 | 23.0333 | 22.9967 | 23.3767 | 23.01 | 22.9133 | 22.5733 | 21.9333 | 20.3633 | 18.82 | 17.7533 | 16.84 | 16.3567 | 15.0567 | 0 | 0 | 0 | 0 | 4.2333 | 101.0667 | 214.8 | 351.7333 | 499.7667 | 639.7667 | 673.4333 | 732.7333 | 749.5333 | 695.2 | 592.6333 | 486.9 | 327.2 | 180.4333 | 67.1333 | 0 | 0 | 0 | 0 | 0
2003 | 7 | 22.6786 | 3.3586 | 127.8954 | 142.7103 | 141.1257 | 108.9374 | 83.2684 | 126.4484 | 161.8013 | 154.2813 | 256.5887 | 19.2194 | 19.1903 | 18.571 | 18.229 | 18.1097 | 19.6613 | 21.2903 | 22.6097 | 23.7613 | 24.8806 | 25.6323 | 26.4032 | 27.0226 | 27.0032 | 26.6484 | 26.5613 | 25.9677 | 25.2355 | 24.1032 | 22.5774 | 21.6548 | 20.5677 | 19.9419 | 19.4452 | 0 | 0 | 0 | 0 | 0.6129 | 83.0645 | 209.7097 | 349.4839 | 505.9677 | 571.9677 | 700.3871 | 757.2903 | 772.0968 | 629.2903 | 559.0645 | 462.0323 | 328.6129 | 171.6129 | 56.9355 | 0 | 0 | 0 | 0 | 0
2003 | 8 | 23.1821 | 3.0978 | 138.3968 | 138.7686 | 122.165 | 84.8301 | 63.3196 | 102.6738 | 145.8502 | 154.1043 | 218.5094 | 20.4323 | 20.1774 | 20.0903 | 19.7161 | 19.4645 | 20.1645 | 21.4613 | 23.1 | 24.5161 | 25.4839 | 26.3645 | 26.6161 | 26.7387 | 27.0387 | 26.6129 | 26.429 | 25.7419 | 24.8194 | 23.6839 | 22.9806 | 21.8968 | 21.3484 | 20.8645 | 20.629 | 0 | 0 | 0 | 0 | 0 | 16.0323 | 162.5484 | 292.3548 | 450.5806 | 552.3871 | 636.7742 | 612.0323 | 628.871 | 595.8387 | 494.5161 | 400.5161 | 263.7419 | 122.1613 | 15.871 | 0 | 0 | 0 | 0 | 0
2003 | 9 | 17.5625 | 3.5783 | 154.8219 | 136.408 | 102.4444 | 61.7759 | 47.1415 | 73.2549 | 121.2651 | 151.2607 | 176.0667 | 14.8933 | 14.35 | 13.89 | 13.5033 | 13.2067 | 13.2733 | 14.8767 | 16.6867 | 18.2733 | 19.7267 | 20.8633 | 21.3833 | 21.81 | 21.91 | 21.95 | 21.7067 | 21.0533 | 19.5133 | 18.22 | 17.2033 | 16.5233 | 16.1033 | 15.1167 | 15.4633 | 0 | 0 | 0 | 0 | 0 | 0.9 | 96.7667 | 234.6333 | 369.1 | 486.1333 | 537.0667 | 569.1 | 543.1667 | 496.8 | 403.3333 | 293.3333 | 163.2667 | 32 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 10 | 11.3984 | 3.1856 | 158.2678 | 120.5924 | 73.1668 | 38.233 | 33.6926 | 46.9232 | 94.096 | 141.4315 | 129.7984 | 8.7484 | 8.0613 | 7.8323 | 7.6323 | 7.2548 | 7.1452 | 8.2645 | 10.3 | 12.0323 | 13.2516 | 14.2871 | 15.0935 | 15.7742 | 15.9903 | 15.9645 | 15.4258 | 14.2839 | 12.7806 | 12.0194 | 11.3484 | 10.9806 | 10.2258 | 9.5419 | 9.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2258 | 157.4839 | 288.1935 | 382 | 442.9355 | 447.5806 | 463.8065 | 390.3226 | 302.6774 | 171.1935 | 53.7419 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 11 | 5.7871 | 4.6115 | 99.3542 | 71.0589 | 37.4346 | 22.5816 | 21.8433 | 24.7403 | 49.556 | 86.1785 | 65.1222 | 4.44 | 4.2733 | 3.8967 | 3.75 | 3.78 | 3.7967 | 3.5733 | 4.5267 | 5.4767 | 6.3433 | 7.2967 | 7.87 | 8.39 | 8.65 | 8.3867 | 7.6067 | 7.04 | 6.7233 | 6.35 | 5.9233 | 5.6933 | 5.45 | 4.88 | 4.7733 | 0 | 0 | 0 | 0 | 0 | 0 | 0.033333 | 48 | 125.1333 | 186.7 | 249.2333 | 271.3333 | 265.1 | 209.4667 | 141.0333 | 65.4 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2003 | 12 | 0.1698 | 4.7377 | 104.6903 | 72.9209 | 34.9698 | 19.7139 | 19.3919 | 21.268 | 47.1807 | 88.774 | 58.9221 | -0.47097 | -0.87097 | -0.92903 | -1.2194 | -1.3355 | -1.429 | -1.5065 | -1.329 | -0.42581 | 0.46452 | 1.2419 | 1.9097 | 2.4258 | 2.5355 | 2.3871 | 1.6484 | 1.0452 | 0.70323 | 0.32903 | 0.096774 | -0.12903 | -0.26774 | -0.44194 | -0.34063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2903 | 94.3226 | 188.871 | 224.4839 | 238.9355 | 259.9677 | 197.129 | 142.8387 | 61.1935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 1 | -6.3643 | 4.9856 | 117.9291 | 84.0146 | 42.7494 | 22.7836 | 22.099 | 25.5804 | 55.9703 | 100.074 | 69.2638 | -6.6806 | -6.8677 | -7.1258 | -7.5645 | -7.9613 | -8.2419 | -8.2258 | -8.1 | -7.6194 | -6.8968 | -6.1613 | -5.6258 | -5.1097 | -4.8 | -4.7 | -4.7839 | -5.0548 | -5.3742 | -5.429 | -5.6774 | -5.9677 | -6.0968 | -6.2387 | -6.4433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4839 | 113 | 182.3226 | 253.1613 | 275.5484 | 299.2581 | 227.5161 | 186.7419 | 106.129 | 12.9355 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 2 | -2.2112 | 4.2787 | 169.15 | 123.5299 | 69.2199 | 34.5054 | 30.8275 | 41.9877 | 92.5662 | 149.1601 | 121.4182 | -4.125 | -4.2786 | -4.2714 | -4.4643 | -4.6214 | -4.4036 | -4.6179 | -3.7893 | -2.8714 | -1.8286 | -0.83571 | -0.032143 | 0.50714 | 0.7 | 0.65357 | 0.43571 | -0.082143 | -0.83571 | -1.2071 | -1.8214 | -2.0679 | -2.3643 | -2.9143 | -3.9321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.4643 | 198.4286 | 315.4643 | 393.4643 | 429.6786 | 461.25 | 412.1071 | 333.6429 | 212.9643 | 86.6429 | 0.92857 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 3 | 5.047 | 5.1559 | 137.9451 | 116.8654 | 82.0506 | 49.355 | 40.4943 | 59.8 | 99.2984 | 130.7156 | 140.7608 | 3.6581 | 3.3097 | 3.4613 | 3.3355 | 3.1161 | 2.8935 | 3.4677 | 4.3645 | 4.9806 | 5.7323 | 6.4806 | 6.9194 | 7.1871 | 7.4419 | 7.5194 | 7.2839 | 6.8581 | 6.0871 | 5.2032 | 4.8 | 4.6419 | 4.3161 | 4.0871 | 3.9839 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1935 | 170.2581 | 250.8387 | 375.5161 | 472.9355 | 482.2581 | 440.4839 | 374.5484 | 346.2581 | 265.1935 | 141.4839 | 33.2903 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 4 | 10.3689 | 5.0622 | 156.939 | 155.1688 | 130.3136 | 85.3585 | 61.1249 | 94.1399 | 139.8156 | 159.436 | 216.8236 | 7.6333 | 7.36 | 7.1667 | 6.77 | 6.3733 | 6.71 | 8.2 | 9.83 | 11.3333 | 12.72 | 13.63 | 14.24 | 14.42 | 14.48 | 14.33 | 13.7 | 12.8867 | 11.9267 | 10.6067 | 9.82 | 9.57 | 8.89 | 8.4233 | 7.8333 | 0 | 0 | 0 | 0 | 0 | 9.9333 | 165.5 | 314.2 | 474.9333 | 580.5 | 640.6667 | 684.6333 | 631.8 | 557.6 | 488.0333 | 355.4667 | 210.9 | 87.2667 | 2.3333 | 0 | 0 | 0 | 0 | 0
2004 | 5 | 15.5312 | 4.2769 | 119.0683 | 125.2672 | 120.017 | 93.3533 | 75.5615 | 111.1115 | 142.6849 | 139.2666 | 207.2097 | 12.7774 | 12.4806 | 12.3806 | 11.9903 | 12.0032 | 12.529 | 13.6645 | 14.8581 | 15.9032 | 16.8032 | 17.6484 | 18.771 | 19.2613 | 19.8355 | 19.9484 | 19.2323 | 18.5129 | 17.7677 | 16.4129 | 15.2968 | 14.5935 | 13.9194 | 13.4032 | 12.7548 | 0 | 0 | 0 | 0 | 0.80645 | 84.9032 | 181.3548 | 273.5806 | 385.0323 | 505.1613 | 547.0323 | 602.6129 | 583.8065 | 549.3548 | 474.0323 | 379.1935 | 259.129 | 114.4194 | 32.6129 | 0 | 0 | 0 | 0 | 0
2004 | 6 | 19.9189 | 3.5039 | 120.0115 | 140.5139 | 145.2075 | 114.7794 | 89.0135 | 132.5003 | 163.8574 | 149.0155 | 255.9069 | 16.61 | 16.3167 | 16.1233 | 15.5767 | 15.71 | 17.1533 | 18.53 | 20.0767 | 21.0133 | 22.0033 | 22.8267 | 23.4 | 23.6267 | 23.6933 | 23.6233 | 23.4067 | 22.9467 | 22.1933 | 21.34 | 20.08 | 18.8533 | 18.1 | 17.7567 | 17.0933 | 0 | 0 | 0 | 0 | 4.5667 | 110.3333 | 242.3333 | 369.3667 | 505.3 | 608.4667 | 695.4333 | 695.8333 | 679.2333 | 617.0667 | 577.5 | 462.5 | 318.6333 | 185.5 | 69.7 | 0 | 0 | 0 | 0 | 0
2004 | 7 | 21.9345 | 3.6099 | 119.6597 | 134.0365 | 132.7474 | 103.3932 | 80.8447 | 119.5814 | 150.168 | 142.3279 | 232.9422 | 18.9774 | 18.5968 | 18.3871 | 17.9097 | 17.8839 | 19.0452 | 20.471 | 21.7581 | 22.9194 | 24.0581 | 24.9355 | 25.4774 | 25.629 | 25.6871 | 25.4806 | 25.3258 | 24.9161 | 24.1677 | 22.9903 | 21.6258 | 20.9129 | 20.3548 | 19.7452 | 19.1742 | 0 | 0 | 0 | 0 | 0.48387 | 78 | 198.871 | 329.9677 | 448.3226 | 545.4839 | 682.2903 | 664.9032 | 622.871 | 581 | 505.1935 | 404.8065 | 313.5484 | 160.7742 | 54.0968 | 0 | 0 | 0 | 0 | 0
2004 | 8 | 19.9785 | 3.5543 | 128.3524 | 130.5953 | 117.1565 | 84.6421 | 64.7332 | 101.723 | 139.6362 | 144.9429 | 199.7876 | 17.2387 | 16.7935 | 16.3774 | 16.271 | 15.9194 | 16.4871 | 18.1452 | 19.7742 | 20.9871 | 21.8129 | 22.671 | 23.1065 | 23.3774 | 23.4968 | 23.671 | 23.6806 | 23.1548 | 22.1516 | 20.9484 | 19.8677 | 19.5806 | 18.4 | 17.7581 | 17.8129 | 0 | 0 | 0 | 0 | 0 | 17.3226 | 154.3548 | 276.9032 | 401 | 460.2581 | 575.3871 | 582.5161 | 585.9677 | 508.0968 | 441.8065 | 390.9677 | 261.9032 | 121.2903 | 17.129 | 0 | 0 | 0 | 0 | 0
2004 | 9 | 19.6157 | 3.3289 | 179.043 | 150.7039 | 111.6543 | 66.6317 | 50.301 | 81.8349 | 143.4366 | 180.1892 | 201.1722 | 16.4733 | 16 | 15.58 | 15.0733 | 14.7 | 14.7733 | 17.02 | 19.3267 | 21.0867 | 22.47 | 23.45 | 24.2433 | 24.8333 | 25.1167 | 24.8433 | 24.3033 | 23.21 | 21.3133 | 19.9333 | 18.7233 | 17.9067 | 17.3167 | 16.65 | 16.43 | 0 | 0 | 0 | 0 | 0 | 0.73333 | 103.8 | 265.5667 | 419.9333 | 499.9333 | 570.7333 | 659.4333 | 664.1 | 620.2 | 487.2333 | 323.3333 | 177.7667 | 35.3667 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 10 | 12.3962 | 4.2702 | 129.0944 | 97.9947 | 62.9073 | 36.4119 | 32.3809 | 44.0115 | 83.7883 | 119.8948 | 108.9194 | 10.4903 | 9.8839 | 9.6774 | 9.3935 | 9.1065 | 9.0484 | 9.771 | 11.2742 | 12.7581 | 13.8065 | 14.5935 | 15.0968 | 15.6839 | 15.9903 | 16.0032 | 15.5968 | 14.7129 | 13.4032 | 12.971 | 12.5 | 12.171 | 11.5065 | 11.1258 | 10.9452 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1613 | 128.5806 | 239.1935 | 315.9677 | 351.3226 | 367.1613 | 377.0968 | 352.5484 | 257.4194 | 161.9677 | 47.6452 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 11 | 6.8072 | 4.006 | 102.4654 | 73.9675 | 40.1389 | 23.3461 | 22.5737 | 26.3125 | 52.7627 | 89.0193 | 66.7153 | 5.6867 | 5.55 | 5.3733 | 5.44 | 5.24 | 5.0333 | 4.9267 | 5.6967 | 6.63 | 7.52 | 8.1967 | 8.69 | 9.0567 | 9.1133 | 8.8633 | 8.4567 | 7.7367 | 7.2567 | 7.1233 | 6.7567 | 6.4667 | 6.4 | 6.11 | 6.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1667 | 133.0667 | 208.6333 | 263.7667 | 248.9667 | 247.5333 | 206.1667 | 167.6333 | 73.8333 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2004 | 12 | -1.2855 | 4.9185 | 124.9809 | 85.4234 | 38.2727 | 19.6123 | 19.2518 | 21.5752 | 53.6754 | 105.3863 | 65.8591 | -2.2613 | -2.4677 | -2.7581 | -2.8161 | -3.1903 | -3.3065 | -3.2097 | -3.1355 | -2.0323 | -1.1484 | -0.27097 | 0.28387 | 0.74194 | 1.0032 | 0.95161 | 0.5 | -0.070968 | -0.39032 | -0.56774 | -0.80323 | -1.0645 | -1.3774 | -1.5903 | -1.8531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8065 | 113.8387 | 188.6774 | 272.871 | 280.3548 | 279.3871 | 212.7419 | 164.4516 | 67.6129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 1 | -3.8132 | 4.4894 | 149.4991 | 102.5266 | 47.7656 | 22.497 | 21.6984 | 26.2602 | 67.7939 | 127.2312 | 81.9865 | -4.5516 | -4.8355 | -4.8839 | -4.9548 | -4.9452 | -5.0839 | -5.0581 | -4.9 | -4.4839 | -3.729 | -3.0968 | -2.5774 | -2.2097 | -2.0871 | -2.0258 | -2.3387 | -2.7129 | -3.0484 | -3.4226 | -3.6129 | -4.0419 | -4.1387 | -4.2323 | -4.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7419 | 135.6774 | 200.0968 | 287.2581 | 343.2258 | 344.0645 | 267.0323 | 237.0323 | 130.9032 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 2 | 0.30134 | 3.8751 | 142.2718 | 107.9407 | 63.3192 | 32.757 | 29.4875 | 38.9253 | 78.9028 | 123.8711 | 102.7173 | -1.0643 | -1.1464 | -1.2536 | -1.4214 | -1.3821 | -1.3321 | -1.3679 | -0.87143 | 0.014286 | 0.75714 | 1.425 | 1.9893 | 2.4179 | 2.8607 | 2.7929 | 2.4929 | 1.825 | 1.1036 | 0.63571 | 0.29643 | 0.060714 | -0.41429 | -0.55357 | -0.63214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.1071 | 191.1429 | 294.3571 | 331.6786 | 359.8214 | 352.6786 | 312.25 | 290.9643 | 188.9643 | 84.3571 | 0.89286 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 3 | 1.7819 | 4.566 | 161.4082 | 133.6552 | 90.5975 | 52.4192 | 42.5094 | 63.4984 | 110.8429 | 151.0329 | 159.0457 | -0.067742 | -0.46774 | -0.63871 | -0.92581 | -1.3677 | -1.5323 | -0.80968 | 0.43548 | 1.471 | 2.3839 | 3.3742 | 4 | 4.7032 | 4.9774 | 5.0065 | 4.9516 | 4.571 | 3.5419 | 2.9226 | 2.1548 | 1.7226 | 1.2935 | 0.9 | 0.16452 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3548 | 171.9355 | 282.8065 | 421.871 | 489.2581 | 556.9677 | 552.0323 | 477.3548 | 362.5161 | 293.129 | 143.6129 | 37.2581 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 4 | 11.2383 | 4.6917 | 155.5325 | 150.6267 | 125.0807 | 82.6881 | 60.2231 | 93.4629 | 139.5349 | 159.8843 | 215.8042 | 7.69 | 7.7367 | 7.2533 | 6.9267 | 6.7367 | 6.9133 | 8.87 | 10.6133 | 12.0867 | 13.24 | 14.5567 | 15.26 | 15.81 | 15.93 | 15.8567 | 15.17 | 14.5833 | 13.4067 | 12.13 | 11.0133 | 10.3633 | 9.89 | 9.1567 | 8.5267 | 0 | 0 | 0 | 0 | 0 | 8.9667 | 160.1 | 304.3 | 427.5667 | 529.3333 | 640.3333 | 709.8333 | 654.7 | 594.1667 | 481 | 356.3333 | 219.2 | 90.6 | 2.8667 | 0 | 0 | 0 | 0 | 0
2005 | 5 | 14.0832 | 4.2733 | 124.5872 | 136.5119 | 132.8161 | 101.9116 | 78.6114 | 114.8048 | 147.2193 | 143.6822 | 223.8481 | 10.7065 | 10.5645 | 10.4806 | 9.9613 | 9.9 | 10.9581 | 12.4548 | 13.9258 | 15.3548 | 16.3323 | 17.3452 | 17.5871 | 18.171 | 18.329 | 18.4032 | 18.0129 | 17.471 | 16.471 | 15.0226 | 13.6613 | 12.671 | 11.971 | 11.4 | 10.8419 | 0 | 0 | 0 | 0 | 0.77419 | 88.9355 | 206.7419 | 341 | 455.7419 | 566.6452 | 638.4839 | 600.9032 | 607.0968 | 582.7097 | 468.2581 | 383.0323 | 257.2581 | 139.2581 | 35.5161 | 0 | 0 | 0 | 0 | 0
2005 | 6 | 23.8478 | 3.8321 | 125.2217 | 148.2944 | 153.3717 | 120.4104 | 91.9097 | 138.7196 | 172.0684 | 156.305 | 271.8847 | 19.96 | 19.7233 | 19.2267 | 18.68 | 18.87 | 20.5233 | 22.52 | 24.01 | 25.45 | 26.58 | 27.34 | 27.9167 | 28.1667 | 28.0167 | 28.3933 | 28.2033 | 27.57 | 26.22 | 24.91 | 23.3867 | 22.5333 | 22.0767 | 21.8133 | 20.2567 | 0 | 0 | 0 | 0 | 4.8667 | 116.2333 | 256.9667 | 397.1333 | 539.8667 | 661.3333 | 762.8 | 742.8 | 673.4 | 659.6333 | 626.9333 | 490.1667 | 334.7667 | 189.4667 | 68.8667 | 0 | 0 | 0 | 0 | 0
2005 | 7 | 24.4417 | 3.6395 | 125.8188 | 141.8109 | 141.4821 | 109.5927 | 83.6412 | 128.3578 | 163.6986 | 154.3276 | 253.8199 | 21.1806 | 20.8258 | 20.3032 | 19.8742 | 19.7323 | 21.471 | 23.0806 | 24.5194 | 25.8968 | 26.6548 | 27.7355 | 28.5516 | 28.3806 | 28.471 | 28.4774 | 28.2484 | 27.3839 | 26.5516 | 25.4161 | 24.1613 | 23.3581 | 22.7194 | 22 | 21.6065 | 0 | 0 | 0 | 0 | 0.54839 | 87.1935 | 220.9355 | 346.9032 | 500.3548 | 563.7097 | 664.7419 | 743.1935 | 709.9032 | 645 | 566.2258 | 477.8387 | 318.3226 | 188.0323 | 58.7742 | 0 | 0 | 0 | 0 | 0
2005 | 8 | 23.8499 | 3.18 | 135.5959 | 134.7773 | 118.9635 | 85.1289 | 65.7045 | 106.0445 | 147.8502 | 154.3986 | 212.9758 | 21.0968 | 20.6194 | 19.7677 | 19.5581 | 19.4677 | 20.4226 | 22.1516 | 23.6452 | 24.8161 | 25.8452 | 26.6097 | 26.9774 | 27.4645 | 27.6903 | 27.8839 | 27.6645 | 27.1806 | 26.2677 | 24.8935 | 23.8194 | 23.0258 | 22.1871 | 21.9871 | 21.3548 | 0 | 0 | 0 | 0 | 0 | 18 | 149 | 296.9032 | 403.1613 | 523.5484 | 557.2903 | 647.2903 | 615.3548 | 564.2258 | 508.1935 | 405.9032 | 283.129 | 123.2903 | 16.129 | 0 | 0 | 0 | 0 | 0
2005 | 9 | 20.8742 | 3.4215 | 150.2317 | 130.6103 | 99.2891 | 62.3507 | 48.2378 | 74.4444 | 122.2783 | 150.7922 | 172.6792 | 17.9267 | 17.4767 | 17.0533 | 16.74 | 16.47 | 16.4533 | 18.1967 | 19.9933 | 21.89 | 23.0567 | 24.2267 | 25.09 | 25.7067 | 26.1133 | 25.71 | 25.3133 | 24.4133 | 22.5533 | 20.9533 | 19.9767 | 19.2767 | 19.2267 | 18.7433 | 18.42 | 0 | 0 | 0 | 0 | 0 | 1.0333 | 99.2667 | 228.0333 | 363.5 | 414.7667 | 526.8333 | 564.5667 | 536.1333 | 511.6333 | 416 | 289.5667 | 156.5667 | 36.4 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 10 | 12.9593 | 3.8761 | 139.9969 | 109.9426 | 69.7419 | 38.1427 | 33.7659 | 45.7084 | 85.6794 | 124.8611 | 115.1277 | 11.0742 | 10.629 | 10.3742 | 10.0742 | 9.7645 | 9.4968 | 10.1935 | 11.8839 | 13.4581 | 14.5548 | 15.2903 | 15.7677 | 16.5452 | 16.8323 | 16.5968 | 15.9161 | 14.8871 | 13.9613 | 13.2903 | 12.7194 | 12.3387 | 12.0581 | 11.7226 | 11.5935 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8387 | 157.6774 | 267.8065 | 346.9677 | 391.7419 | 377.1935 | 404.1613 | 312.5161 | 274.0323 | 166.0968 | 50.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 11 | 5.6975 | 5.1794 | 128.2878 | 92.9114 | 47.2266 | 25.3371 | 24.2633 | 28.1579 | 59.8345 | 108.0452 | 80.1972 | 5.1867 | 4.97 | 4.6 | 4.15 | 3.6233 | 3.31 | 3.2467 | 4.07 | 5.0267 | 6.06 | 7.0033 | 7.6933 | 8.0967 | 8.1833 | 8.1333 | 7.5767 | 6.7233 | 6.2433 | 6.13 | 5.4333 | 5.3933 | 5.16 | 5.1633 | 5.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 61.0333 | 164.2 | 259.1 | 327.0333 | 336.2 | 291.8 | 235 | 175.1333 | 73.5667 | 1.5667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005 | 12 | -4.4407 | 4.1687 | 102.2059 | 70.139 | 33.2433 | 18.4748 | 18.1477 | 20.3501 | 46.8722 | 87.6804 | 56.5638 | -5.4968 | -5.4419 | -5.629 | -5.6742 | -5.6839 | -5.5355 | -5.6548 | -5.4032 | -4.7258 | -3.9742 | -3.2452 | -2.7774 | -2.4355 | -2.3645 | -2.6645 | -3.2032 | -3.6419 | -3.9323 | -4.3323 | -4.5677 | -4.7839 | -4.929 | -5.2419 | -5.2125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7097 | 107.871 | 159.7742 | 219.0645 | 240.129 | 239.2258 | 182.1613 | 143.129 | 65.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 1 | 2.1629 | 4.3055 | 102.484 | 71.2567 | 35.4156 | 21.9557 | 21.6138 | 24.0858 | 49.578 | 89.3158 | 64.2396 | 1.4419 | 1.0581 | 0.77419 | 0.45806 | 0.51613 | 0.27742 | 0.65806 | 1.3581 | 2.0871 | 2.7903 | 3.4581 | 3.8097 | 4.0903 | 4.0742 | 3.7613 | 3.2 | 2.8032 | 2.529 | 2.3161 | 2.4161 | 2.1613 | 2.071 | 2.0387 | 1.7467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8065 | 70.871 | 162.0323 | 239.9677 | 277.7419 | 268.8065 | 235.3871 | 172.4516 | 86.5806 | 17.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 2 | -1.958 | 4.2634 | 179.1356 | 127.3276 | 66.9717 | 31.5908 | 28.1943 | 39.7965 | 94.4204 | 157.9998 | 128.4211 | -3.7321 | -3.925 | -4.1893 | -4.6179 | -4.6429 | -4.6643 | -3.9393 | -2.7464 | -1.6393 | -0.60714 | 0.16786 | 0.92857 | 1.0286 | 1.3643 | 1.0036 | 0.48929 | -0.41786 | -1.025 | -1.7571 | -2.1607 | -2.3607 | -2.8464 | -3.2607 | -3.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17857 | 53.8214 | 184.2143 | 319.1071 | 426 | 493.2143 | 490.6429 | 447.5714 | 342.3214 | 223.8571 | 95.6429 | 5.5357 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 3 | 3.6856 | 4.2285 | 152.3077 | 118.4798 | 80.5091 | 49.4945 | 41.4615 | 64.5509 | 115.6639 | 152.9653 | 154.5376 | 1.8903 | 1.571 | 1.4645 | 1.071 | 1.0774 | 1.6581 | 2.8903 | 4.0258 | 4.8613 | 5.6032 | 6.0839 | 6.5065 | 6.6742 | 6.4161 | 5.8323 | 5.3161 | 4.4032 | 4.0032 | 3.6774 | 3.371 | 3.1355 | 2.8452 | 2.3387 | 1.7387 | 0 | 0 | 0 | 0 | 0 | 0 | 27.7097 | 133.2581 | 256.2258 | 374.4516 | 472.2903 | 534.4839 | 526.1613 | 489.4516 | 405.129 | 289.4839 | 159.0968 | 41.1613 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 4 | 12.0226 | 4.4472 | 144.8851 | 135.4478 | 110.5159 | 70.5145 | 51.4869 | 91.9886 | 142.4602 | 158.877 | 212.7403 | 8.79 | 8.3767 | 8.0833 | 7.61 | 7.9967 | 9.8267 | 11.5533 | 12.84 | 14.0267 | 14.9533 | 15.5167 | 15.9133 | 16.17 | 16.2467 | 15.87 | 15.35 | 14.08 | 12.85 | 11.8233 | 11.1533 | 10.95 | 10.0933 | 9.48 | 8.99 | 0 | 0 | 0 | 0 | 0 | 17.1 | 123.4 | 272.0333 | 402.3 | 533.2333 | 630.0333 | 661 | 642.2 | 597.6667 | 506.8333 | 368.6 | 239.4 | 103 | 8.9667 | 0 | 0 | 0 | 0 | 0
2006 | 5 | 15.6516 | 3.4503 | 123.8514 | 128.8751 | 120.909 | 90.9913 | 73.3257 | 118.4061 | 155.9589 | 150.7089 | 234.496 | 12.0548 | 11.9226 | 11.6774 | 11.4548 | 12.9581 | 14.4548 | 15.8032 | 16.8129 | 17.8194 | 18.5129 | 18.9968 | 19.1871 | 19.4355 | 19.3 | 19.0806 | 18.629 | 17.7323 | 16.3871 | 15.3774 | 14.5968 | 14.1548 | 13.6516 | 13.0581 | 12.5806 | 0 | 0 | 0 | 0 | 2.4194 | 62.9032 | 180.5484 | 291.4194 | 412.5484 | 557.6129 | 668.5806 | 733.0968 | 708.7097 | 603.6129 | 501.9677 | 409.6129 | 289.6129 | 161 | 44.2581 | 0 | 0 | 0 | 0 | 0
2006 | 6 | 20.5569 | 3.2653 | 121.6173 | 136.9985 | 139.0914 | 109.1785 | 87.2699 | 142.8614 | 180.7379 | 162.0885 | 275.0944 | 16.5333 | 16.1633 | 16.0067 | 16.1 | 17.6 | 19.0567 | 20.63 | 21.5533 | 22.6367 | 23.61 | 24.4533 | 24.6 | 24.59 | 24.6 | 24.41 | 23.7167 | 22.9567 | 22.0367 | 20.93 | 19.7733 | 19.1233 | 18.1233 | 17.2167 | 16.9467 | 0 | 0 | 0 | 0 | 8.6667 | 94.0667 | 224 | 363.6333 | 479.9667 | 598.5667 | 710 | 766.0333 | 790.9 | 723.7333 | 639.9333 | 522.6333 | 377.8333 | 219.1667 | 81.1667 | 1.9667 | 0 | 0 | 0 | 0
2006 | 7 | 25.0567 | 2.9113 | 125.1485 | 136.4643 | 133.4402 | 101.1222 | 79.4873 | 138.7575 | 181.4635 | 166.7358 | 272.9341 | 21.5161 | 21.5355 | 21.1516 | 21.2548 | 22.0452 | 23.3452 | 24.6323 | 25.7387 | 26.6484 | 27.3774 | 28.0065 | 28.6613 | 28.8129 | 28.8065 | 28.8452 | 28.3968 | 27.6097 | 26.4 | 25.0806 | 24.4645 | 23.7516 | 22.8742 | 22.5935 | 21.8129 | 0 | 0 | 0 | 0 | 2.4194 | 71.2258 | 206.6452 | 344.0968 | 450.871 | 587.4194 | 704.7097 | 780.7097 | 799.9032 | 742 | 633.4516 | 516.8065 | 388.0323 | 236.2903 | 85.3548 | 0.48387 | 0 | 0 | 0 | 0
2006 | 8 | 23.537 | 2.8831 | 136.7083 | 135.3712 | 117.3012 | 81.9491 | 62.2089 | 103.2422 | 146.0471 | 154.4686 | 222.8763 | 20.8161 | 20.4387 | 20.4548 | 20.0323 | 20.6065 | 22.1194 | 23.4839 | 24.6226 | 25.4516 | 26.0516 | 26.7871 | 27.1065 | 27.1613 | 27.0355 | 26.6806 | 26.2129 | 25.2516 | 23.8935 | 23.0548 | 22.4613 | 22.1645 | 21.2387 | 20.8226 | 20.9387 | 0 | 0 | 0 | 0 | 0 | 26.6774 | 142.4839 | 273.7097 | 397.7742 | 532.0968 | 660.2903 | 726.0968 | 705.6774 | 596.6129 | 479.2903 | 374.9032 | 266.0968 | 139.4194 | 27.9032 | 0 | 0 | 0 | 0 | 0
2006 | 9 | 16.9153 | 3.1681 | 144.0981 | 118.1637 | 84.8305 | 52.3297 | 42.1802 | 70.4143 | 119.5982 | 149.0371 | 165.0653 | 14.4733 | 14.17 | 13.9633 | 13.6033 | 13.4433 | 14.81 | 16.3 | 17.6867 | 18.68 | 19.47 | 20.0067 | 20.2667 | 20.6967 | 20.6667 | 20.3133 | 19.4067 | 18.1867 | 16.9533 | 16.5233 | 16.19 | 15.6567 | 15.0667 | 14.6367 | 14.7967 | 0 | 0 | 0 | 0 | 0 | 2.5 | 69.4 | 176.1667 | 297.1333 | 407.3667 | 498.9 | 570.4 | 567.3 | 481.9667 | 388.3 | 287.7333 | 165.9667 | 48.4333 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 10 | 9.4383 | 4.1734 | 158.0045 | 118.3922 | 68.8418 | 34.9888 | 30.3104 | 43.8187 | 91.5113 | 141.5934 | 125.6035 | 7.4935 | 7.2323 | 7.0613 | 6.9323 | 6.4484 | 6.9032 | 8.3806 | 9.7419 | 10.8 | 11.6161 | 12.1226 | 12.4097 | 12.5806 | 12.5161 | 12.1258 | 11.1258 | 10.2 | 9.629 | 9.2677 | 8.8226 | 8.7548 | 8.4452 | 7.9677 | 7.9419 | 0 | 0 | 0 | 0 | 0 | 0 | 24.2903 | 129.4839 | 241.0968 | 355.7742 | 442.6774 | 488.9032 | 462.9355 | 371.1935 | 276.6129 | 165.4839 | 55.3226 | 0.70968 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 11 | 6.0967 | 3.8986 | 110.4228 | 76.5156 | 39.3498 | 21.6061 | 20.7722 | 24.8584 | 56.0121 | 96.9518 | 68.9264 | 4.57 | 4.4267 | 4.29 | 4.0467 | 3.8967 | 3.7667 | 4.38 | 5.7233 | 6.89 | 7.86 | 8.4433 | 9.0867 | 9.3367 | 9.22 | 8.6367 | 7.4067 | 6.93 | 6.1467 | 5.93 | 5.6233 | 5.14 | 4.95 | 4.8067 | 4.8133 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0333 | 43.5333 | 125.8 | 207.1 | 259.7667 | 283.0333 | 272.3 | 226.0333 | 156.3667 | 73.5 | 5.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006 | 12 | 1.1314 | 4.3275 | 113.3001 | 75.6952 | 32.4934 | 16.4774 | 16.2447 | 18.2079 | 48.2058 | 96.3292 | 59.0698 | -0.10968 | -0.26774 | -0.57742 | -0.85161 | -0.85806 | -0.77742 | -0.55161 | 0.093548 | 1.1129 | 1.8226 | 2.4806 | 2.9548 | 3.1065 | 3.2968 | 2.8 | 2.3548 | 2.1516 | 2.1645 | 1.829 | 1.5484 | 1.3065 | 1.0742 | 0.74839 | 0.32813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8065 | 82.9032 | 167.6452 | 229.6452 | 262.4194 | 250.7419 | 210.0323 | 144.1613 | 60.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 1 | -2.0747 | 4.8116 | 114.378 | 78.8112 | 37.6129 | 21.0661 | 20.7252 | 23.7314 | 53.3751 | 98.6009 | 67.7066 | -2.8806 | -3.1226 | -3.2581 | -3.4968 | -3.6226 | -3.7323 | -3.7548 | -2.9452 | -2.2742 | -1.4871 | -0.90323 | -0.4129 | -0.23226 | -0.15484 | -0.35161 | -0.86452 | -1.3516 | -1.6161 | -1.5871 | -1.7581 | -1.9935 | -2.4516 | -2.6774 | -2.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8387 | 79.871 | 170.3226 | 244.6452 | 289.0323 | 287.2581 | 249.6774 | 177.7097 | 95.3871 | 19.0323 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 2 | -7.7232 | 4.9807 | 158.4424 | 109.2985 | 57.9761 | 31.2276 | 29.0712 | 38.2131 | 87.1532 | 143.6593 | 110.8021 | -8.9964 | -9.2679 | -9.5214 | -9.5464 | -9.675 | -9.6929 | -9.3893 | -8.6107 | -7.6 | -6.7286 | -6.0786 | -5.6179 | -5.4036 | -5.3929 | -5.5393 | -6.15 | -6.7786 | -7.1571 | -7.5071 | -7.5714 | -7.8286 | -8.0679 | -8.4214 | -8.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17857 | 41.7143 | 150.6429 | 267.6786 | 360.7143 | 419.8214 | 437.6071 | 393.8214 | 311.0714 | 198.0714 | 75.6071 | 2.3214 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 3 | 5.9458 | 4.6237 | 146.2453 | 112.9784 | 74.6421 | 45.4637 | 38.8809 | 58.7987 | 105.881 | 143.7129 | 145.1935 | 3.6613 | 3.4097 | 3.271 | 3.1548 | 3.1613 | 3.4129 | 4.5355 | 5.9387 | 6.9581 | 7.8968 | 8.5226 | 8.9355 | 9.1194 | 9.1871 | 8.7355 | 8.1774 | 7.1774 | 6.3065 | 5.9548 | 5.7032 | 5.4419 | 5.1 | 4.8645 | 4.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6452 | 112.3871 | 231.3548 | 356.3226 | 454.9355 | 524.6129 | 522.4516 | 460.4839 | 364.0645 | 259.5806 | 141.7742 | 36.0323 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 4 | 8.321 | 4.8306 | 138.2384 | 129.5137 | 105.608 | 70.4418 | 54.2717 | 87.1308 | 129.6701 | 146.5218 | 195.2278 | 5.3367 | 4.79 | 4.51 | 4.3567 | 4.62 | 6.0867 | 7.5467 | 9.0067 | 10.1733 | 11.1133 | 11.6967 | 11.7233 | 12.0633 | 12.0167 | 11.6333 | 11.2 | 10.3333 | 9.21 | 8.4633 | 7.7433 | 7.3067 | 6.6267 | 6.1867 | 5.96 | 0 | 0 | 0 | 0 | 0 | 14 | 112.1 | 241.9333 | 373.4333 | 487.4333 | 591.2333 | 637.6 | 622.5 | 527.3 | 434.2667 | 331.2667 | 212.2667 | 92.0667 | 8.0667 | 0 | 0 | 0 | 0 | 0
2007 | 5 | 17.8266 | 4.2608 | 140.1778 | 144.0821 | 134.1328 | 98.9707 | 78.5682 | 135.1692 | 182.3419 | 175.8082 | 274.4812 | 13.7742 | 13.3581 | 13.1258 | 13.1194 | 14.0839 | 15.5065 | 17.0419 | 18.5065 | 19.6613 | 20.6419 | 21.7452 | 22.4484 | 22.7419 | 22.5581 | 22.1258 | 21.3032 | 20.3581 | 19.0968 | 17.971 | 17.0129 | 16.3516 | 15.7839 | 15.2935 | 14.229 | 0 | 0 | 0 | 0 | 2.3871 | 66.5484 | 198.2258 | 350.5484 | 478.8387 | 640.2258 | 773.5806 | 828.5484 | 830.0968 | 747.6774 | 609.4516 | 486.4516 | 341.2903 | 184.2581 | 49.4194 | 0 | 0 | 0 | 0 | 0
2007 | 6 | 22.1206 | 3.6042 | 127.0003 | 142.6061 | 143.8656 | 111.1674 | 88.0782 | 146.2466 | 186.9415 | 168.3612 | 294.4069 | 18.54 | 18.2 | 18.1133 | 18.14 | 19.5267 | 21.09 | 22.35 | 23.5867 | 24.4267 | 25.3367 | 25.5933 | 25.9433 | 26.0467 | 25.2033 | 25.0967 | 24.8 | 24.1167 | 22.9733 | 22.1367 | 21.1 | 20.4967 | 19.92 | 19.2233 | 18.9333 | 0 | 0 | 0 | 0 | 8.8 | 93.2333 | 230.4667 | 380.7667 | 525.7667 | 677.1 | 777.4667 | 830.2333 | 836.7 | 796.5667 | 683.3333 | 535.7667 | 375.3333 | 224.9667 | 86.8333 | 2.4333 | 0 | 0 | 0 | 0
2007 | 7 | 23.2453 | 3.2003 | 131.2501 | 145.8154 | 142.8052 | 106.9828 | 82.4074 | 143.3221 | 187.2687 | 172.2802 | 290.9005 | 19.5968 | 19.2161 | 18.8677 | 18.7871 | 19.871 | 21.3774 | 22.7065 | 24.1516 | 25.2968 | 26.3548 | 27.1032 | 27.2548 | 27.5774 | 27.2387 | 26.6839 | 26.3387 | 25.771 | 24.6677 | 23.3968 | 22.6581 | 21.6645 | 20.8516 | 20.4484 | 20.0065 | 0 | 0 | 0 | 0 | 2.7742 | 76.9032 | 217.3226 | 354.4516 | 510.2258 | 663.2581 | 781.8387 | 857.2258 | 836.0968 | 768.1935 | 649.4839 | 536.2581 | 395.8387 | 243.1935 | 88.0323 | 0.51613 | 0 | 0 | 0 | 0
2007 | 8 | 23.7917 | 2.746 | 137.8591 | 133.5319 | 114.1824 | 79.1935 | 60.7527 | 107.6746 | 154.4152 | 161.7209 | 225.6613 | 21.2968 | 20.8097 | 20.5419 | 20.2613 | 20.5387 | 21.971 | 23.3387 | 24.471 | 25.5097 | 26.4032 | 26.9935 | 27.3226 | 27.4355 | 26.929 | 26.7613 | 26.3 | 25.3645 | 24.2677 | 23.5 | 23.029 | 22.4452 | 22.2968 | 21.6548 | 21.5581 | 0 | 0 | 0 | 0 | 0 | 25.3871 | 140.1613 | 266.7419 | 379.2903 | 515.5161 | 657.6129 | 733.0645 | 724.8387 | 586.4516 | 486.6452 | 414.7419 | 302.7419 | 153.4194 | 29.2581 | 0 | 0 | 0 | 0 | 0
2007 | 9 | 20.1804 | 3.6292 | 186.9191 | 151.4092 | 107.0087 | 59.9666 | 44.4735 | 83.9373 | 154.4585 | 194.2552 | 214.6528 | 16.5967 | 16.2367 | 15.7633 | 15.5133 | 15.5 | 16.9333 | 18.9133 | 20.5467 | 22.2 | 23.51 | 24.1867 | 25.1667 | 25.3233 | 25.1133 | 24.72 | 23.6833 | 22.0433 | 20.8633 | 20.2467 | 19.57 | 18.8833 | 18.1533 | 17.5167 | 17.1467 | 0 | 0 | 0 | 0 | 0 | 3.4 | 90.4 | 247.4 | 409.1667 | 543.2 | 646.1 | 716.1667 | 713.4 | 637.4333 | 515.3333 | 368.3333 | 206.1333 | 55.2 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 10 | 15.1222 | 4.1237 | 148.4052 | 110.9681 | 65.992 | 34.1952 | 30.1936 | 43.0122 | 88.5522 | 134.0001 | 117.0444 | 12.8806 | 12.4032 | 12.2226 | 11.9032 | 11.7742 | 12.2387 | 13.4935 | 14.9065 | 16.3677 | 17.2968 | 18.2097 | 18.8452 | 19.2194 | 19.1387 | 18.5839 | 17.6742 | 16.1129 | 15.6387 | 15.2097 | 14.5871 | 14.1968 | 13.6194 | 13.2484 | 13.1613 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6774 | 123.2258 | 239.3226 | 337.1935 | 405.0968 | 429.1613 | 418.6774 | 358.0968 | 260.5161 | 161.5161 | 54.3226 | 0.25806 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 11 | 4.304 | 4.2444 | 134.9622 | 93.8582 | 45.128 | 21.7222 | 20.6734 | 25.2503 | 62.5095 | 115.0394 | 80.9236 | 2.87 | 2.6433 | 2.3533 | 2.1833 | 2.01 | 1.8667 | 2.8767 | 4.1333 | 5.2867 | 5.97 | 6.4933 | 6.86 | 7.1133 | 6.8767 | 6.5 | 5.66 | 5.0633 | 4.8533 | 4.3667 | 4.02 | 3.65 | 3.42 | 3.0867 | 3.14 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0333 | 53.4667 | 155.1667 | 243.8 | 307.4 | 333.6 | 317.5667 | 262.7 | 177.8667 | 82.5 | 7.0667 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2007 | 12 | -2.1549 | 3.9087 | 83.0653 | 58.2719 | 27.8027 | 17.8425 | 17.6365 | 18.7969 | 37.3492 | 70.9584 | 49.894 | -2.7968 | -2.9387 | -3.3194 | -3.4645 | -3.6419 | -3.8194 | -3.7 | -3.0613 | -2.3032 | -1.6 | -0.69355 | -0.86129 | -0.6 | -0.64839 | -0.90645 | -1.2742 | -1.5323 | -1.6871 | -1.8548 | -1.8452 | -1.9387 | -2.1645 | -2.3258 | -2.7219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9677 | 67.3871 | 142.1613 | 198.0323 | 229.6774 | 217.9032 | 177.0968 | 112.2903 | 44.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 1 | -4.2732 | 4.8183 | 120.2158 | 82.0539 | 38.1726 | 20.8352 | 20.4454 | 23.544 | 55.2202 | 103.5836 | 70.0619 | -5.8677 | -6.2129 | -6.2968 | -6.2 | -6.2258 | -6.0613 | -5.7968 | -5.0742 | -4.0258 | -2.9548 | -2.0581 | -1.5 | -1.271 | -1.3548 | -1.729 | -2.671 | -3.271 | -3.8903 | -4.3581 | -4.6935 | -4.9194 | -5.0871 | -5.3516 | -5.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3226 | 85.871 | 180.8065 | 255.5806 | 302.8387 | 301.0968 | 253.7097 | 178.6774 | 93.0323 | 17.2903 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 2 | -5.099 | 4.1815 | 139.6797 | 100.97 | 57.1463 | 33.0592 | 30.7076 | 38.6423 | 78.2901 | 125.4119 | 105.247 | -5.7571 | -5.9393 | -6.3143 | -6.5107 | -6.7071 | -6.8464 | -6.6143 | -5.9536 | -5.2 | -4.6179 | -4.0393 | -3.7 | -3.4857 | -3.4929 | -3.5036 | -3.85 | -4.3714 | -4.625 | -4.6714 | -4.9786 | -5.0214 | -5.2143 | -5.4464 | -5.5143 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21429 | 42.5 | 147.75 | 257.2143 | 346.3214 | 404.1071 | 410.8214 | 373.5357 | 287.9643 | 180.0714 | 71.75 | 3.6786 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 3 | 1.4655 | 4.1398 | 148.9261 | 115.8157 | 76.4176 | 44.5235 | 37.1281 | 58.6997 | 107.9614 | 146.105 | 149.6411 | -0.21613 | -0.4871 | -0.77419 | -1.1387 | -1.2 | -0.77742 | -0.090323 | 1 | 1.8613 | 2.6258 | 3.129 | 3.7065 | 4.2355 | 4.3452 | 4.1484 | 3.6516 | 2.7258 | 2.1419 | 1.7226 | 1.5839 | 1.2903 | 0.98387 | 0.7871 | -0.083871 | 0 | 0 | 0 | 0 | 0 | 0 | 25.3548 | 123.9355 | 247.9355 | 368.2258 | 461.8387 | 516.129 | 510.4839 | 486.8065 | 390 | 274.4839 | 148.9032 | 37.2903 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 4 | 9.6171 | 4.4583 | 145.8794 | 130.0229 | 106.341 | 71.7452 | 55.0947 | 95.0359 | 147.6177 | 164.8445 | 211.8458 | 6.7867 | 6.5833 | 6.2433 | 5.8967 | 6.32 | 7.6433 | 8.8233 | 9.99 | 11.04 | 12.1533 | 12.8567 | 13.44 | 13.5667 | 13.38 | 13.0833 | 12.5567 | 11.5467 | 10.27 | 9.4367 | 8.5233 | 8.13 | 7.86 | 7.4767 | 7.2033 | 0 | 0 | 0 | 0 | 0 | 19.0333 | 118.6667 | 239.1333 | 377.3333 | 495.6667 | 591.9667 | 665.4667 | 673.5333 | 641.2 | 539.5333 | 381 | 232.7667 | 99.3667 | 9.6333 | 0 | 0 | 0 | 0 | 0
2008 | 5 | 13.7378 | 4.2446 | 125.5188 | 136.1569 | 130.9905 | 97.9175 | 73.6441 | 112.6892 | 148.9578 | 146.5025 | 236.0659 | 10.0645 | 9.871 | 9.4968 | 9.429 | 10.5065 | 12.0677 | 13.5548 | 14.5 | 15.2677 | 16.1129 | 16.9065 | 17.5258 | 17.9194 | 17.8806 | 17.7129 | 17.2935 | 16.471 | 15.1806 | 13.8452 | 13.1742 | 12.0871 | 11.4613 | 10.9645 | 10.4129 | 0 | 0 | 0 | 0 | 2.8387 | 70.3871 | 207.2581 | 359.4516 | 474.0645 | 563.0645 | 633.9032 | 680.7742 | 686 | 664.2903 | 529.5806 | 372.9677 | 245.0645 | 135.1935 | 40.7419 | 0 | 0 | 0 | 0 | 0
2008 | 6 | 21.5522 | 3.8222 | 122.1725 | 141.6838 | 143.9583 | 112.4589 | 87.7885 | 132.1247 | 163.7428 | 149.9189 | 261.0917 | 17.92 | 17.5033 | 17.27 | 17.3067 | 18.6067 | 19.8067 | 21.15 | 22.3267 | 23.26 | 24.24 | 24.65 | 25.2733 | 25.6533 | 25.6833 | 25.2167 | 24.6133 | 23.9833 | 23.1167 | 21.7167 | 20.84 | 20.1933 | 19.5633 | 19.08 | 18.28 | 0 | 0 | 0 | 0 | 8.3667 | 89.6667 | 229.9333 | 380.5333 | 523.6667 | 627.5667 | 731.6333 | 753.1 | 705.3333 | 654.6333 | 559.5667 | 425.5333 | 295.9667 | 194.0333 | 83.8 | 2.8667 | 0 | 0 | 0 | 0
2008 | 7 | 23.5419 | 3.3454 | 136.4775 | 150.3843 | 147.3728 | 110.8097 | 85.0177 | 150.3808 | 197.8907 | 182.2066 | 302.8293 | 19.7161 | 19.5323 | 19.1194 | 19.0355 | 20.0323 | 21.5935 | 23.1161 | 24.3548 | 25.5742 | 26.5613 | 27.1774 | 27.6032 | 27.4645 | 27.5871 | 27.3968 | 26.8871 | 26.2355 | 24.9839 | 23.7742 | 22.8194 | 22 | 21.3226 | 20.8871 | 20.2323 | 0 | 0 | 0 | 0 | 2.3871 | 74.0645 | 222.0323 | 391.0323 | 533.3226 | 649.871 | 759 | 869.6774 | 884.5806 | 818.871 | 710.7419 | 588.2903 | 426.0968 | 249.4194 | 87.7742 | 0.74194 | 0 | 0 | 0 | 0
2008 | 8 | 22.6204 | 3.0591 | 163.0831 | 164.041 | 141.9056 | 92.807 | 64.1824 | 118.8608 | 176.6287 | 186.8301 | 274.1035 | 19.3613 | 19.0323 | 18.7097 | 18.4871 | 18.9387 | 20.5 | 21.9806 | 23.3581 | 24.5968 | 25.3548 | 25.9419 | 26.3645 | 26.6677 | 26.7484 | 26.2903 | 25.6935 | 24.7032 | 23.5258 | 22.5129 | 22.0903 | 21.2548 | 20.6645 | 20.2452 | 19.8677 | 0 | 0 | 0 | 0 | 0 | 30.6452 | 173.9677 | 359.129 | 532.2581 | 674.0323 | 773.0645 | 832.0968 | 831.1935 | 741.4839 | 619.6129 | 482.9355 | 334.1935 | 164.5484 | 29.3226 | 0 | 0 | 0 | 0 | 0
2008 | 9 | 18.8911 | 2.7556 | 150.4039 | 123.7127 | 88.6586 | 51.6078 | 39.7886 | 68.9976 | 122.2593 | 153.6463 | 169.0847 | 16.1333 | 15.8233 | 15.6033 | 15.3233 | 15.2333 | 16.53 | 18.05 | 19.7033 | 20.93 | 21.7467 | 22.2967 | 22.59 | 22.6867 | 22.65 | 22.3567 | 21.55 | 20.2867 | 19.26 | 18.6233 | 18.25 | 17.6833 | 17.0433 | 16.4833 | 16.55 | 0 | 0 | 0 | 0 | 0 | 2.6 | 71.3667 | 200.0333 | 330.2 | 448.3 | 524.8333 | 552.5 | 549.6667 | 489 | 401.2333 | 288.5 | 158.7333 | 41.0667 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 10 | 11.5895 | 3.5887 | 156.081 | 116.5226 | 68.0081 | 34.0092 | 29.8782 | 43.9411 | 92.0259 | 140.5094 | 121.6801 | 9.0516 | 8.8903 | 8.429 | 8.3419 | 8.0129 | 8.7097 | 10.2806 | 11.9032 | 13.1903 | 14.1935 | 14.5903 | 14.971 | 15.2516 | 15.3 | 14.7613 | 13.6774 | 12.6419 | 12.1903 | 11.7387 | 11.371 | 10.8355 | 10.3258 | 10.0387 | 9.4516 | 0 | 0 | 0 | 0 | 0 | 0 | 21.871 | 129.3226 | 257.0645 | 359.4194 | 421.1613 | 436.5806 | 422.0645 | 368.4194 | 275.3226 | 171.4194 | 57.1613 | 0.51613 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 11 | 4.1061 | 4.1736 | 136.6625 | 93.8897 | 44.7379 | 22.2043 | 21.3159 | 25.4273 | 63.3669 | 117.1407 | 80.4528 | 2.7633 | 2.5367 | 2.32 | 1.92 | 1.6433 | 1.7633 | 2.4467 | 3.77 | 4.8167 | 5.74 | 6.49 | 6.8067 | 6.9567 | 6.8467 | 6.3 | 5.3267 | 4.9333 | 4.4933 | 4.14 | 3.9067 | 3.5233 | 3.1567 | 2.9367 | 3.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46667 | 47.5333 | 152.9 | 243.9667 | 307.4 | 334.5 | 319.2667 | 266.9 | 174.7333 | 78.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008 | 12 | -4.8658 | 5.004 | 122.4557 | 82.0965 | 33.9596 | 16.5699 | 16.3363 | 18.2101 | 49.7147 | 102.8495 | 62.5933 | -5.6452 | -5.9548 | -6.2097 | -6.371 | -6.5387 | -6.7161 | -6.4935 | -5.8903 | -5.1194 | -4.3677 | -3.8129 | -3.3258 | -3.2774 | -3.329 | -3.5613 | -4.0806 | -4.1387 | -4.1387 | -4.2516 | -4.2774 | -4.2839 | -4.5258 | -5.1161 | -5.3375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.871 | 88.6452 | 180.0323 | 247.7419 | 281.5484 | 267.5161 | 225.3548 | 144.0968 | 57.129 | 0.32258 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 1 | -8.546 | 3.9879 | 140.1698 | 92.9773 | 41.3849 | 22.397 | 21.9959 | 25.6926 | 64.4365 | 122.4422 | 80.4522 | -9.7323 | -9.9194 | -10.0677 | -10.1516 | -10.2129 | -10.1161 | -9.8968 | -9.3871 | -8.5548 | -7.5935 | -6.8871 | -6.4419 | -6.1774 | -6.0871 | -6.3323 | -6.9419 | -7.6161 | -8.1129 | -8.3806 | -8.8097 | -9.1 | -9.2581 | -9.4581 | -9.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 90.9032 | 193.1935 | 281.0968 | 343.3548 | 351.2903 | 310.6129 | 214.9032 | 110.3871 | 21.5161 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 2 | -1.8433 | 4.6086 | 163.2625 | 117.0547 | 62.7793 | 32.0285 | 29.3589 | 37.7792 | 84.8644 | 142.6677 | 116.7902 | -3.3321 | -3.6714 | -4.1286 | -4.425 | -4.5071 | -4.55 | -3.9 | -2.6857 | -1.4607 | -0.61071 | 0.060714 | 0.64643 | 1.175 | 1.225 | 1.1143 | 0.51071 | -0.31786 | -1.0321 | -1.4393 | -1.8214 | -2.4714 | -2.5571 | -2.8821 | -3.1786 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17857 | 46.25 | 164.3214 | 291.6429 | 392 | 438.8571 | 458.1429 | 424.6071 | 321.5714 | 188.5 | 73.0714 | 3.8214 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 3 | 4.2661 | 4.3118 | 156.0271 | 123.4078 | 81.2521 | 45.1002 | 36.425 | 58.4735 | 109.4965 | 149.8484 | 154.582 | 1.971 | 1.5935 | 1.4871 | 1.3355 | 0.90968 | 1.5516 | 2.5613 | 3.7968 | 5.0258 | 6.2258 | 7.1613 | 7.5935 | 8.0387 | 8.2419 | 8.0419 | 7.1258 | 5.9548 | 4.9258 | 4.2355 | 3.6742 | 3.2871 | 2.9871 | 2.529 | 2.1323 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9677 | 135.7742 | 267.6774 | 393.0645 | 489.3226 | 535.3226 | 538.129 | 488.5806 | 385.4194 | 267.6129 | 144.6774 | 37.4194 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 4 | 8.6833 | 4.6319 | 133.4337 | 125.3466 | 103.7786 | 68.3076 | 51.281 | 82.0812 | 124.8236 | 140.9977 | 186.7236 | 6.1533 | 5.6867 | 5.47 | 5 | 5.1367 | 6.57 | 7.6867 | 8.9233 | 9.9767 | 10.85 | 11.49 | 11.98 | 12.3867 | 12.2333 | 11.93 | 11.43 | 10.4333 | 9.4833 | 8.7467 | 8.2533 | 7.8133 | 7.44 | 7.02 | 6.3067 | 0 | 0 | 0 | 0 | 0 | 13.8333 | 106.5 | 244.8333 | 376.1667 | 486.2667 | 555 | 574.7667 | 568.8 | 528.6667 | 425.9333 | 315 | 195.3667 | 83.1667 | 7.0667 | 0 | 0 | 0 | 0 | 0
2009 | 5 | 15.4312 | 3.6935 | 124.5891 | 129.1806 | 121.7931 | 90.3725 | 71.9959 | 126.7117 | 170.2953 | 161.1373 | 246.5591 | 11.8839 | 11.3323 | 11.1935 | 11.0226 | 12.0097 | 13.5484 | 15.271 | 16.7097 | 17.7355 | 18.4774 | 19.1355 | 19.6871 | 19.829 | 19.8 | 19.429 | 18.529 | 17.6161 | 16.2032 | 14.8839 | 14.1806 | 13.7645 | 13.1742 | 12.6484 | 12.2839 | 0 | 0 | 0 | 0 | 2.4516 | 63.1613 | 176.3548 | 310.4194 | 441.129 | 553.2258 | 646.7097 | 713 | 717.8387 | 669.8065 | 590.6774 | 474.871 | 333.3548 | 177.5806 | 46.8387 | 0 | 0 | 0 | 0 | 0
2009 | 6 | 19.9061 | 3.1625 | 120.5425 | 134.8665 | 135.6815 | 106.9255 | 87.5339 | 140.5438 | 175.6676 | 157.6876 | 265.0042 | 16.83 | 16.5567 | 16.2767 | 16.3233 | 17.2033 | 18.29 | 19.3067 | 20.62 | 21.7033 | 22.5433 | 23.08 | 23.4167 | 23.6033 | 23.85 | 23.3733 | 22.8133 | 22.05 | 20.8333 | 19.6 | 19.0433 | 18.33 | 17.5967 | 17.41 | 17.0933 | 0 | 0 | 0 | 0 | 7.9667 | 83.5667 | 210.9667 | 347.1333 | 470.7667 | 598.0667 | 704.8333 | 771.9333 | 752.1 | 678.3 | 580.7333 | 488.1333 | 366.2333 | 215.8333 | 81.2333 | 2.3 | 0 | 0 | 0 | 0
2009 | 7 | 20.8847 | 2.8965 | 127.5433 | 141.029 | 137.3315 | 103.9219 | 81.2812 | 131.785 | 169.5641 | 158.6422 | 261.3011 | 17.5774 | 17.3774 | 16.8387 | 16.6806 | 17.6548 | 19.1677 | 20.6774 | 21.8581 | 22.7516 | 23.7032 | 24.1032 | 24.4839 | 24.6516 | 24.4903 | 24.0194 | 23.5323 | 22.9452 | 22.1645 | 21.1774 | 20.1516 | 19.7032 | 19.1097 | 18.4548 | 17.9581 | 0 | 0 | 0 | 0 | 2.0323 | 64.3871 | 192.5806 | 346.9677 | 486.1613 | 623.1935 | 713.6774 | 747.8065 | 729.5806 | 696.4516 | 566.6452 | 468.6452 | 346.3226 | 208.2581 | 78.3226 | 0.19355 | 0 | 0 | 0 | 0
2009 | 8 | 21.2332 | 3.3925 | 138.7497 | 136.2491 | 118.8375 | 82.0826 | 61.8506 | 108.5175 | 156.253 | 162.389 | 228.9207 | 18.3677 | 18.1903 | 18.1387 | 17.8677 | 18.2387 | 19.7774 | 21.0065 | 22.071 | 23.2097 | 23.8032 | 24.471 | 24.5452 | 24.9258 | 24.6194 | 24.071 | 23.5677 | 22.7097 | 21.6774 | 20.9613 | 20.4548 | 19.8613 | 19.4516 | 18.9161 | 18.6935 | 0 | 0 | 0 | 0 | 0 | 26.8387 | 133.4516 | 276.3226 | 435.5806 | 543.7419 | 627.3871 | 682.1935 | 699.8065 | 630.0645 | 541.0968 | 425.1935 | 294.4516 | 150.3548 | 27.6129 | 0 | 0 | 0 | 0 | 0
2009 | 9 | 18.4031 | 2.6097 | 168.9053 | 137.6883 | 98.8546 | 59.3519 | 46.0784 | 81.2673 | 142.3096 | 176.9994 | 198.9556 | 15.2967 | 15.04 | 15.03 | 14.93 | 14.8467 | 16.08 | 17.6633 | 19.1733 | 20.6133 | 21.4633 | 22.1533 | 22.67 | 22.7367 | 22.3433 | 21.7933 | 20.9 | 19.6167 | 18.8167 | 18.11 | 17.53 | 16.9067 | 16.37 | 16 | 15.59 | 0 | 0 | 0 | 0 | 0 | 3.3667 | 83.3333 | 215.2667 | 356.2333 | 502.2333 | 607.5667 | 688.1 | 682.3333 | 586.6333 | 469.8 | 336.4667 | 190.1667 | 53.4333 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 10 | 9.4542 | 3.7769 | 103.9526 | 79.1929 | 50.9022 | 32.2029 | 29.3076 | 38.1689 | 67.9514 | 97.3556 | 88.6008 | 7.9903 | 7.9452 | 7.7806 | 7.6258 | 7.3129 | 7.7839 | 8.5839 | 9.5161 | 10.2548 | 11.0387 | 11.5742 | 11.8355 | 11.6871 | 11.5484 | 11.2645 | 10.7032 | 10.1097 | 9.6258 | 9.5 | 9.0677 | 8.871 | 8.5935 | 8.3581 | 8.329 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5806 | 93.1613 | 164.4194 | 251.871 | 316.8387 | 331.5484 | 308.7419 | 273.5161 | 206.1613 | 120.2581 | 40.8387 | 0.48387 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 11 | 7.5993 | 3.5625 | 105.7045 | 70.873 | 36.4519 | 20.8333 | 20.1191 | 24.4989 | 56.5223 | 95.7082 | 67.5208 | 5.75 | 5.6 | 5.3533 | 5.14 | 4.8833 | 5.7467 | 6.4133 | 7.2767 | 8.3867 | 9.3233 | 10.17 | 11.06 | 11.01 | 10.52 | 9.6533 | 8.88 | 8.3133 | 8.14 | 7.6167 | 7.3 | 6.9267 | 6.6067 | 6.2367 | 6.0767 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 40.2333 | 118.1 | 191.4667 | 244.8333 | 275.5333 | 273.3 | 237.1 | 157.1 | 75.3 | 6.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009 | 12 | -2.5871 | 4.1101 | 102.5456 | 68.886 | 31.2455 | 18.2461 | 18.0279 | 19.8347 | 46.3443 | 88.7927 | 57.3047 | -3.3581 | -3.3645 | -3.2548 | -3.371 | -3.3677 | -3.3452 | -3.2742 | -2.8645 | -2.2355 | -1.7839 | -1.2903 | -1.0613 | -0.89032 | -0.94194 | -1.3194 | -1.7806 | -2.2548 | -2.4903 | -2.771 | -3.0871 | -3.1903 | -3.4419 | -3.7452 | -3.575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.129 | 78.2903 | 159.7097 | 224.3548 | 253.4516 | 245.4194 | 214.1613 | 134.1613 | 56.2903 | 0.19355 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 1 | -5.5773 | 4.0538 | 132.1099 | 89.9391 | 40.7866 | 21.8206 | 21.3992 | 24.6231 | 59.1616 | 113.2874 | 76.4549 | -6.5871 | -6.7484 | -6.9581 | -7.1419 | -7.1581 | -7.1774 | -7.2129 | -6.6387 | -5.7968 | -5.0806 | -4.3581 | -3.8452 | -3.6097 | -3.5355 | -3.729 | -4.1774 | -4.6032 | -4.971 | -5.271 | -5.4065 | -5.5968 | -6.0161 | -6.0194 | -6.2367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5806 | 90.5806 | 194.6774 | 278.2903 | 327.8065 | 324.1935 | 282.0645 | 200.871 | 103.6774 | 19.7097 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 2 | -2.6954 | 3.5491 | 133.7788 | 99.4494 | 57.9998 | 36.4786 | 34.5208 | 40.5427 | 74.3154 | 118.6241 | 103.0074 | -4.2036 | -4.2393 | -4.4714 | -4.5214 | -4.5464 | -4.6357 | -4.3321 | -3.5929 | -2.55 | -1.75 | -1.0929 | -0.62857 | -0.45357 | -0.53929 | -0.76429 | -1.0571 | -1.5679 | -1.95 | -2.2214 | -2.6393 | -2.6607 | -2.9571 | -3.3464 | -3.9679 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14286 | 40.2143 | 146.6786 | 260 | 349.7143 | 402.8571 | 400.3214 | 365.4286 | 273.4286 | 166 | 64.5714 | 2.8214 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 3 | 5.2628 | 3.7648 | 138.2887 | 108.1541 | 74.8657 | 47.0181 | 40.2092 | 61.1403 | 106.9995 | 139.3402 | 141.7823 | 2.6903 | 2.4742 | 2.2258 | 2.2548 | 1.929 | 2.6194 | 3.8968 | 5.2839 | 6.3742 | 7.5194 | 8.2871 | 8.8452 | 9.0419 | 9.1419 | 8.8935 | 8.1645 | 6.8839 | 5.8194 | 5.2419 | 4.5742 | 4.0387 | 3.7871 | 3.4742 | 2.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 25.1613 | 116.7097 | 226.4839 | 339.5806 | 426.871 | 470.1935 | 486.4516 | 472.8387 | 383.7097 | 269.5484 | 147.2581 | 37.9677 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 4 | 12.5686 | 4.5611 | 149.1328 | 136.5553 | 111.7262 | 72.0053 | 52.8356 | 98.6442 | 154.3791 | 170.01 | 219.1708 | 9.0933 | 8.85 | 8.5933 | 8.4067 | 8.8167 | 10.3233 | 11.7467 | 13.14 | 14.36 | 15.2267 | 16.06 | 16.8 | 17.3233 | 17.31 | 16.8933 | 16.16 | 15.0667 | 13.5767 | 12.2367 | 11.48 | 10.7333 | 10.26 | 9.76 | 9.43 | 0 | 0 | 0 | 0 | 0 | 18.0333 | 125.5333 | 272.1667 | 421.7667 | 533.1667 | 611.4333 | 655.3667 | 664.9 | 616.5 | 534.1 | 416.3333 | 267.2 | 113.8 | 9.8 | 0 | 0 | 0 | 0 | 0
2010 | 5 | 16.5883 | 3.7083 | 128.6766 | 135.482 | 127.7609 | 95.3711 | 74.5823 | 120.4733 | 159.9412 | 155.5707 | 246.1384 | 12.8645 | 12.6871 | 12.3613 | 12.2968 | 13.3871 | 14.8226 | 16.3935 | 17.6226 | 18.771 | 19.4323 | 19.9419 | 20.3613 | 20.4355 | 20.5903 | 20.0323 | 19.6323 | 18.8548 | 17.7742 | 16.8387 | 15.8645 | 15.1548 | 14.5903 | 13.9806 | 13.429 | 0 | 0 | 0 | 0 | 2.7097 | 64.7742 | 184.2903 | 327.6129 | 453.9032 | 586.6129 | 691.7742 | 760.3226 | 746.129 | 651.6774 | 521.6452 | 417.7097 | 291.2258 | 161.4516 | 45.4839 | 0 | 0 | 0 | 0 | 0
2010 | 6 | 21.7399 | 3.3333 | 119.5883 | 133.0445 | 134.7989 | 106.2009 | 84.997 | 139.2996 | 177.2285 | 159.8676 | 269.7347 | 19.0233 | 18.7167 | 18.4633 | 18.4233 | 19.29 | 20.0867 | 21.3067 | 22.2433 | 23.13 | 24.0133 | 24.5967 | 25.0333 | 25.58 | 25.5533 | 24.9467 | 24.2467 | 23.5933 | 22.6233 | 21.5033 | 20.7633 | 20.1467 | 19.7867 | 19.41 | 19.2767 | 0 | 0 | 0 | 0 | 8.6333 | 90.8 | 211.7667 | 339.3 | 471.2667 | 578.0333 | 681.9667 | 773.4 | 790.1 | 758.3667 | 620.0333 | 505.2333 | 359.8333 | 204.5333 | 78 | 2.3667 | 0 | 0 | 0 | 0
2010 | 7 | 25.4534 | 3.2527 | 136.6126 | 151.1523 | 147.1913 | 109.965 | 85.1159 | 150.2374 | 196.435 | 180.4984 | 302.6774 | 22.0903 | 21.4774 | 21.1065 | 21.0548 | 21.9581 | 23.3161 | 24.671 | 25.8871 | 27.0677 | 28.0871 | 28.7097 | 29.5 | 29.8194 | 29.8903 | 29.529 | 28.771 | 27.8452 | 26.6774 | 25.4677 | 24.7871 | 24.2516 | 23.6645 | 22.9129 | 22.3387 | 0 | 0 | 0 | 0 | 2.3548 | 71.6774 | 215.6129 | 378.129 | 534.8065 | 689.4516 | 807.129 | 879.6129 | 863.2258 | 800.9677 | 697.3548 | 568.4516 | 419.2258 | 245.7742 | 89.9032 | 0.58065 | 0 | 0 | 0 | 0
2010 | 8 | 24.7766 | 3.1169 | 159.4792 | 154.4059 | 132.0821 | 88.0042 | 63.9942 | 120.8826 | 179.8272 | 188.8577 | 266.797 | 21.4452 | 21.1226 | 20.8806 | 20.5355 | 20.971 | 22.3968 | 23.7258 | 24.8903 | 25.8871 | 26.9065 | 27.7581 | 28.4581 | 28.8645 | 28.9032 | 28.8097 | 28.1806 | 27.5258 | 26.2581 | 24.9935 | 24.3419 | 23.8484 | 23.2645 | 22.7581 | 21.9129 | 0 | 0 | 0 | 0 | 0 | 30.7419 | 166.3226 | 313.2258 | 471.6452 | 622.7097 | 751.7097 | 815.7742 | 826.7742 | 744.6452 | 619.5806 | 497.6129 | 341.6452 | 170.4194 | 30.3226 | 0 | 0 | 0 | 0 | 0
2010 | 9 | 18.4539 | 3.7764 | 154.6195 | 126.5606 | 90.9125 | 55.1005 | 43.4321 | 73.8133 | 127.9189 | 159.9162 | 177.0444 | 16.26 | 16.08 | 15.8233 | 15.5333 | 15.2467 | 16.2533 | 17.1867 | 18.3933 | 19.47 | 20.33 | 21.11 | 21.71 | 22.0733 | 22.2 | 21.8967 | 21.1567 | 19.7467 | 18.9433 | 18.3867 | 17.7133 | 17.3733 | 16.89 | 16.5167 | 16.6 | 0 | 0 | 0 | 0 | 0 | 2.7667 | 74.7 | 198.0667 | 310.9667 | 444.9333 | 557.1667 | 598.6 | 588.3 | 521.6667 | 418.0333 | 308.5333 | 177.6667 | 47.6667 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 10 | 13.2331 | 3.7608 | 188.4986 | 134.587 | 75.4988 | 35.7383 | 30.5842 | 48.5008 | 112.1255 | 173.5604 | 147.0188 | 10.5 | 10.0194 | 9.5839 | 9.2226 | 8.9323 | 9.6935 | 11.6065 | 13.3935 | 15.0194 | 16.2258 | 17.3129 | 18 | 18.3 | 18.2935 | 17.6032 | 16.3226 | 14.6419 | 13.6548 | 12.9839 | 12.3323 | 11.4097 | 11.0548 | 10.7613 | 10.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 24.7419 | 143.4516 | 281.7097 | 410.8387 | 507.871 | 546.4839 | 522.0968 | 470.0968 | 347.1935 | 207.0323 | 66.5484 | 0.3871 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 11 | 5.2749 | 4.1458 | 141.8226 | 98.5856 | 47.7907 | 23.0196 | 21.9757 | 27.1077 | 66.6427 | 121.29 | 85.3861 | 3.52 | 3.17 | 2.9833 | 2.9667 | 2.6 | 2.9267 | 3.75 | 4.9567 | 6.2433 | 7.2833 | 8.0933 | 8.69 | 8.8767 | 8.78 | 7.71 | 6.9 | 6.1933 | 5.6567 | 5.17 | 4.58 | 4.24 | 3.9367 | 3.62 | 3.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 54.8 | 160.1333 | 257.8 | 327.9 | 355.1333 | 332.2667 | 273.6 | 192.4333 | 86.7667 | 7.6333 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010 | 12 | -5.0957 | 4.0148 | 113.7044 | 75.8835 | 33.3938 | 19.2018 | 18.9699 | 20.8143 | 50.1899 | 98.1699 | 62.5087 | -6.4548 | -6.3839 | -6.7258 | -6.9774 | -6.9258 | -6.7226 | -6.5484 | -5.6323 | -4.6484 | -3.6387 | -2.9903 | -2.6645 | -2.4839 | -2.6645 | -3.1452 | -3.5645 | -4.5 | -4.8839 | -5.1419 | -5.4032 | -5.7355 | -5.8806 | -6.2323 | -6.3094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7419 | 82.3871 | 172.4194 | 246.129 | 282.3548 | 274.3226 | 229.7419 | 144.8387 | 58.0968 | 0.19355 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## OfficeMedium
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | OfficeMedium
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the Medium Office from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | HVAC values were tweaked to reflect individual AC units with central gas heat and individual controls
Building Height [m] | 11.89 |  |  | Setback temps are implemented (not done in PNNL reference building)
Total building conditioned floor area [m2] | 4982 |  |  | Occupany is 268 people
People Density: Occ (m2/person) | 24
People Density: Unocc (m2/person) | 343.7
Building occupancy day - From: | 0
Building occupancy day - To: | 4
Equivalent full-load occupancy hours - From: | 8
Equivalent full-load occupancy hours - To: | 18
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 17.35 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 25.84 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 6.06 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 2.04 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 7.18 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 0.94 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 2607 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 1 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 3.5 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1.15 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 3078 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 3078 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 3078 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 3078 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 1 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.08 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.43 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 268 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 38253
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 2.7
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 2.7
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 397.47 | 0 | 264.99 | 0 | 397.47 | 0 | 264.99 | 0 | 1660.73
U-value | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.363 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 195.84 | 0 | 130.56 | 0 | 195.84 | 0 | 130.56 | 0 | 0
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 0
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0
Shading Correction Factor (SCF) | bar: 2.7 S to 2.7 Roof
Shading Device Factor (SDF) | bar: 2.7 S to 2.7 Roof
Area Summary | 2.7 S: m2; 2.7 SE: ft2
Total roof area [m2] | 2.7 S: 1660.73; 2.7 SE: 17836.2402
Total opaque wall area [m2] | 2.7 S: 1324.92; 2.7 SE: 14229.6408
Total window [m2] | 2.7 S: 652.8; 2.7 SE: 7011.072
Total Envelope Area [m2] | 2.7 S: 3638.45; 2.7 SE: 39076.953
Window to Wall Ratio | 2.7 S: 0.33008
IPLV Calculator | bar: 2.7 S to 2.7 SE
Relative COP100: for Relative Load 100% | 2.7 S: 1; 2.7 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 2.7 S: 0.9; 2.7 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 2.7 S: 0.82; 2.7 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 2.7 S: 0.5; 2.7 SE: Refer to the right figure
Weighting of 100% Load | 2.7 S: 0.01; 2.7 SE: From ARI 550/590
Weighting of 75% Load | 2.7 S: 0.42; 2.7 SE: From ARI 550/591
Weighting of 50% Load | 2.7 S: 0.45; 2.7 SE: From ARI 550/592
Weighting of 25% Load | 2.7 S: 0.12; 2.7 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 2.7 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11

## RetailStandalone
Hourly & Monthly Energy Calculation Inputs - Non Residential
Notes: This Info is used to populate ISM headers and set weather file path
Building Type | RetailStandalone
Year Built | 2010
Path to Weather File to Use for Analysis | c:\epw\ord.epw
Program/People |  |  | Notes: | This was originally generated from the Retail Standalone from the PNNL 2013 Code DOE Reference Building
Terrain class | 0.8 |  |  | HVAC is ptacs with gas furnace, CAV distribution, use type 19
Building Height [m] | 6.1 |  |  | Occupany is 371 people
Total building conditioned floor area [m2] | 2294 |  |  | Windows only on the S wall
People Density: Occ (m2/person) | 9.5
People Density: Unocc (m2/person) | 63.6
Building occupancy day - From: | 0
Building occupancy day - To: | 5
Equivalent full-load occupancy hours - From: | 10
Equivalent full-load occupancy hours - To: | 18
Heat Gain per Person [W/person] | 120
Internal Temperature Set Point |  |  | [Table] Ventilation system specification <source: EN 15243, Table E.1> | [6 empty] | HVAC Distribution Loss Factors
Occupied Internal set point for heating [°C] | 21.1 |  | system code / heat distribution by / cold distribution by / individual heating control | [6 empty] | Waste* | Heating | Cooling
Unoccupied Internal set point for heating [°C] | 17.7 |  | 1 | 1. No airco system / Water or Water&Air / NA / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Internal set point for cooling [°C] | 24.3 |  | 2 | 2. No airco system / Water or Water&Air / NA / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Internal set point for cooling [°C] | 27.6 |  | 3 | 3. No airco system / Air / NA / Yes | [5 empty] | 0 | 0 | 0
|  |  | 4 | 4. No airco system / Air / NA / No | [5 empty] | 0 | 0.36 | 0
Internal Appliance Heat Gain [W/m2] |  |  | 5 | 5. Single duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Occupied Electric Appiance Power Density | 4.76 |  | 6 | 6 .Single duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Unoccupied Electric Appiance Power Density | 1.8 |  | 7 | 7. Single duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Occupied Natural Gas Appiance Power Density | 0 |  | 8 | 8. Single duct system / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Unoccupied Natural Gas Appiance Power Density | 0 |  | 9 | 9. Single duct system / Air / Air / No | [5 empty] | 0 | 0.36 | 0
|  |  | 10 | 10. Dual duct system / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting |  |  | 11 | 11. Dual duct system / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Occupied Interior Lighting Power Intensity [W/m2] | 13.72 |  | 12 | 12. Dual duct system / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Unoccupied Interior Lighting Power Intensity [W/m2] | 3.25 |  | 13 | 13. Dual duct system / Air / Water / Yes | [5 empty] | 0.08 | 0 | 0.01
Exterior Lighting Power [W] | 1525 |  | 14 | 14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Lighting daylighting sensor control fraction | 1 |  | 15 | 15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Lighting occupancy sensor control fraction | 1 |  | 16 | 16. Single duct , Terminal reheat / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Lighting constant illumination control fraction | 1 |  | 17 | 17. Constant volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
|  |  | 18 | 18. Constant volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Building System |  |  | 19 | 19. Constant volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
HVAC system type (See Table at right) | 19 |  | 20 | 20. Constant volume / Air / Air / Yes | [5 empty] | 0.04 | 0 | 0
Cooling System |  |  | 21 | 21. Constant volume / Air / Air / No | [5 empty] | 0 | 0.36 | 0
Cooling System COP [KW/KW] | 3 |  | 22 | 22. Variable air volume / Water or Water&Air / Water / Yes | [5 empty] | 0.03 | 0.08 | 0.01
Cooling system Integrated Partial Load index Value (IPLV) | 1.05 |  | 23 | 23. Variable air volume / Water or Water&Air / Air / Yes | [5 empty] | 0 | 0.08 | 0
Heating System |  |  | 24 | 24. Variable air volume / Water or Water&Air / Air / No | [5 empty] | 0 | 0.25 | 0
Heating Energy Carrier | 2 |  | 25 | 25. Fan coil system, 2-pipe | [5 empty] | 0.04 | 0.08 | 0.01
Heating System Efficiency [KW/KW] | 0.8 |  | 26 | 26. Induction system, 2-pipe non change over | [5 empty] | 0.08 | 0 | 0.01
Ventilation System |  |  | 27 | 27. Induction system, 2-pipe change over | [5 empty] | 0.04 | 0.08 | 0.01
Ventilation type | 1 |  | 28 | 28. Induction system, 3-pipe | [5 empty] | 0 | 0 | 0
Occupied Ventilation Air Intake Rate [L/s] | 3600 |  | 29 | 29. Induction system, 4-pipe | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Intake Rate [L/s] | 3600 |  | 30 | 30. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0.04 | 0.08 | 0.01
Occupied Ventilation Air Exhaust Rate [L/s] | 3600 |  | 31 | 31. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams) | [5 empty] | 0 | 0 | 0
Unoccupied Ventilation Air Exhaust Rate [L/s] | 3600 |  | 32 | 32. Embedded cooling system floors, walls or ceilings | [5 empty] | 0.04 | 0.08 | 0.01
Heat recovery efficiency | 0 |  | 33 | 33. Room units including single duct units | [5 empty] | 0 | 0 | 0
Exhaust air recirculation percentage | 0% |  | 34 | 34. Direct expansion single split system | [5 empty] | 0 | 0 | 0
Pump System |  |  | 35 | 35. User Input (put values in at right) | [5 empty] | 0 | 0.1 | 0
Pump control for cooling | 1 |  | *Waste = simultaneous heating and cooling | [5 empty] | Loss Factors Set from C41 Pulldown
Pump control for heating | 1 |  | Chiller COP Ranges | [5 empty] | Selected | 0 | 0.25 | 0
Fan System |  |  | Chiller Type |  | MW | Mbtu/hr | ARI COP
Specifiec fan power [W/(L/s)] | 0.43 |  | Vapor compression chillers
Fan flow control factor | 1 |  | Reciprocating |  | up to 1.5 | up to 5.1 | 3.8-4.6
Domestic Hot Water System |  |  | Rotary | Screw | 0.3-7 | 1 - 24 | 4.1-5.6
DHW Demand [m3/yr] | 268 |  |  | Scroll
DHW System Efficiency | 0.8 |  |  | Rolling piston
DHW Distribution Efficiency | 0.8 |  |  | Rotating vane
DHW Energy Carrier | 2 |  | Centrifugal |  | 0.3-35 | 1-120 | 5.0 - 7.9
Building Energy Management System |  |  | Absorption chillers
Type of BEM system installed | 1 |  | single stage |  | 0.3-6 | 1-21 | 0.7
|  |  | Double-stage |  | 0.3-8 | 1-27 | 1.2
Envelope/Enclosure System |  |  | Direct-fired |  | 0.3-5.2 | 1-18 | 1.7
Heat Capacity (Thermal Mass)
Interior Heat Capacity [J/K/m2] | 98010
Envelope Heat Capacity [J/K/m2] | 144263
Infiltration @ 75 Pa [m3/h/m2] using Envelope Surface Area
Occupied Envelope Infiltration Rate [m3/h/m2] | 9.6
Envelope Infiltration Rate Unoccupied [m3/h/m2] | 9.6
Wall/Roof | S | SE | E | NE | N | NW | W | SW | Roof
Area [m2] | 246.89 | 0 | 257.68 | 0 | 330.83 | 0 | 257.68 | 0 | 2294
U-value | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.511 | 0.27
Solar Absorption coefficient | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Thermal Emissivity | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Window | S | SE | E | NE | N | NW | W | SW | Skylight
Area [m2] | 83.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.4
U-value [W/m2K] | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 2.653 | 5.72
SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426 | 0.506
Shading Correction Factor (SCF) | bar: 9.6 S to 9.6 Roof
Shading Device Factor (SDF) | bar: 9.6 S to 9.6 Roof
Area Summary | 9.6 S: m2; 9.6 SE: ft2
Total roof area [m2] | 9.6 S: 2294; 9.6 SE: 24637.56
Total opaque wall area [m2] | 9.6 S: 1093.08; 9.6 SE: 11739.6792
Total window [m2] | 9.6 S: 83.89; 9.6 SE: 900.9786
Total Envelope Area [m2] | 9.6 S: 3470.97; 9.6 SE: 37278.2178
Window to Wall Ratio | 9.6 S: 0.071276
IPLV Calculator | bar: 9.6 S to 9.6 SE
Relative COP100: for Relative Load 100% | 9.6 S: 1; 9.6 SE: Refer to the right figure
Partial Load COP75 Relative Load 75% | 9.6 S: 0.9; 9.6 SE: Refer to the right figure
Partial Load COP50 Relative Load 50% | 9.6 S: 0.82; 9.6 SE: Refer to the right figure
Partial Load COP25 Relative Load 25% | 9.6 S: 0.5; 9.6 SE: Refer to the right figure
Weighting of 100% Load | 9.6 S: 0.01; 9.6 SE: From ARI 550/590
Weighting of 75% Load | 9.6 S: 0.42; 9.6 SE: From ARI 550/591
Weighting of 50% Load | 9.6 S: 0.45; 9.6 SE: From ARI 550/592
Weighting of 25% Load | 9.6 S: 0.12; 9.6 SE: From ARI 550/593
IPLV (Integrated Partial Load Value) (for Cell C64) | 9.6 S: 0.817
Note on B9: Terrain Class: 0.8 = city/urban 0.9 = suburban, partial shelter 1.0 = open space
Note on B12: Occupant Density : Occupied Times Area per Occupant in m2/person during the "occupied" period. Typical office is 20 m2/person
Note on B13: Occupant Density: Unoccupied Occupant density during times of day considered unoccupied. Typically 150 -200 m2/person
Note on B14: Occupancy Start Day 1 = Mon, 7 - Sun enter the start day of major occupancy, which is Monday for most offices
Note on B15: Occupancy End Day 1 = Mon, 7 - Sun enter the ending day of major occupancy, which is Friday for most offices
Note on B16: Start of hour for start of occupancy (i.e. if Most people arrive between 8 and 9am put in 8)
Note on B17: Start of hour of unoccupied times (i.e. if most people leave between 5pm and 6pm put in 18)
Note on B18: Heat Gain Per Person Typically this is about 80 W/person for offices
Note on B27: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the occupied times. This is typically 5 - 15 W/m2
Note on B28: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B30: Electrical Appliance Heat Gain: Occupied Electrical plugload power density in W/m2, during the unoccupied times. This is typically 0.5 - 2 W/m2
Note on B35: Exterior Lighting Power Lights assumed to be on only at night. If lights are on at all times derate the power so the yearly energy us is equivalent to using only at night
Note on B36: Daylight Sensors Fraction: 1.0 = No Sensor 0.8 = Photocell Dimming See EN/ISO 16193 Annex F/G3
Note on B37: Occupancy Sensors Fraction 1.0 = No occupancy Sensor 0.8 = Occupancy sensors for > 60% of load See EN/ISO 16193 Annex F/G3
Note on B38: Constant Illumination Control Fraction 1.0 = No Constant Illum Control Operating 0.9 = Constant Illum Control Operating See EN/ISO 16193 Annex F/G3
Note on B44: IPLV is ratio of seasonal COP to full load COP i..e IEER/EER or SEER/EER. Use calculator at bottom to get IPLV from partial load values. See AHR 550/990 for more details. Values range from 0.5 to 1.5
Note on B46: Heating Fuel 1 = Electricity 2 = Natural Gas
Note on B49: Ventilation 1 = Mechanical Only 2 = Mechanical + Natural 3 = Natural Only
Note on B50: Rate of Outdoor Air Intake for Ventilation in L/s Typcially this is 20 L/s/person or greater as per ASHRAE 62.1
Note on B52: Rate of Ventilation Exhaust in L/s. Exhaust = Intake for a balanced building.
Note on B54: Heat Recovery Efficiency 0.4 = Loading cold with A/C 0.6 = heat pipes 0.6 = two element system 0.65 = heat exchange plates or heat pipes 0.7 = slowy rotating or intermittent heat exchangers see NEN 2916 Table 6
Note on B57: Cooling Pump Control Factor: 0.0 = No Pumps in Cooling System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on B58: Heating Pump Control Factor: 0.0 = No Pumps in Heating System 0.5 = Automatic speed control > 50% of capacity 1.0 = All other Cases See NEN 2916.9.4.3
Note on K58: Set by System Type Pulldown Above
Note on B60: Specific Fan Power (SFP) SFP = Fan Power/Volume Flow Rate [W/L/s] Typical values are 1-1.5. <1.0 is high efficiency 1.0-2.0 is good efficiency 2.0-3.0 is fair efficiency > 3.0 is low efficiency
Note on B61: Fan Flow Control Factor: 1.0 = No Fan Control 0.75 = Inlet Blade Adjust (no cooling, or cooling dist. by water) 0.65 = Inlet Blade Adjust (cooling dist. by air) 0.65 = Variable Speed Control (no cooling or cooling dist by water) 0.5 = Variable Speed Control (ooling distributed by air) see NEEN 2916:7.3.3.4
Note on B63: DHW Demand Use 10L/per/day for offices
Note on B64: DHW System Efficiency: 1.4 = Heat Pump 0.9 = High Efficiency Electric , District Heating, or CoGen Heating 0.75 = Electric or High Efficiency Gas 0.65 = Gas 0.60 = Steam see NEN 12.6.2 Table 34
Note on B65: DHW Distribution Efficiency 1.0 = All taps within 3m of Heat Generation 0.8 = Some taps more than 3m from Heat Generation 0.6 = Circulation System or Unknown Distribution
Note on B66: DHW Fuel Type 1 = Electric 2 =Natural Gas
Note on B68: Building Energy Management System (BEM): 1 = no/minimal BEM installed 2 = automatica control and scheduling of systems 3 = automatic control + FDD
Note on B72: Interior Envelope Heat Capacity (Thermal Mass): (J/K/kg/m2 floor area) 80,000 = Very Light: No thermal mass elements 110,000 = Light floor slab, no mass in walls 260,000 = Medium floor slab, light mass in walls 370,000 = Heavy floor slab, large mass in walls ref ISO 13790 !2.3
Note on B73: Envelope Heat Capacity (Thermal Mass): Exposed thermal mass in J/K/m2 envelope area 30,000: Very Light: Glass or Stone Panel Curtain Wall, No thermal mass 45,000 = Light: 1 - 4 in of Thermal Mass 65,000 = Medium: 4 - 8 in of Thermal Mass 100,000 = Heavy: 8-12 in of Thermal Mass 150,000 = Very Heavy: > 12 in of Thermal Mass
Note on B75: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B76: Infiltration Rate:m3/h/m2 @ 75 Pa based on envelope area 3.0 = very tight (glass curatin wall) 6.0= tight commercial building (panel curtain wall) 10.0 = average (normal masonry, tight frame) 15.0 = leaking building (leaky masonry, normal frame) 20.0 = very leaky building (leaky frame) Ref : Tamura 1976, Emerich 2005, AIVC TN44
Note on B86: Shading Correction Factor (SCF) SCF accounts for external shading devices like overhangs and fins
Note on B87: Shading Device Factor accounts for user or automatically controlled blinds 1.0 = No blinds 0.5 = user/manual blind control 0.35 = automatic control of blinds See NEN 2916 Table 11